## Sheet1
Verification of commutation reactance using built-in HVDC transformer option in ElmHvdclcc element
In the case of a built-in HVDC transformer option in the ElmHvdclcc element, the value of the programmed commutation reactance is included always in the simulation. As such, this option, as it will be seen further, generates correct results only when the source impedance (i.e. the grid reactance) can be neglected i.e. the commutating voltage is found at the HV side of the converter transformer. In all other cases, deviations may occur with this option and therefore, an external representation of the transformer is recommended. The same considerations and conclusions will apply to the Rectifier/Inverter element (ElmRes). In this example, the use of a large shunt compensation has the effect of creating a commutating voltage at the HV transformer side. Other equipment may also have the same effect (e.g. synchronous condensers, STATCOM, etc). The results of EMT simulation are compared with the results of the load flow model. An RMS simulation has not been executed, since the RMS model is based on the same equations as the load flow model - identical results are expected as in load flow. Note 1: the Load flow and RMS models use and are influenced by the commutation reactance. Note 2: Whenever the commutating voltage is not located at the HV bus of the HVDC transformer, the value of the commutation reactance is dependent on the operation scenario and grid topology (i.e. its value will change every time that the impedance between the HVDC and the commutating voltage bus changes). Note 3: In almost all cases, the commutation reactance must include the transformer reactance.
| System ratings |  |  | Zb_HV | 160 | Ohm
| UHV | 400 | kV | Zb_HVDC | 40 | Ohm
| Uhvdc | 200 | kV
| Skss @ HVDC | 10000 | MVA | Skss is not precisely reported.
| Shvdc | 1000 | MVA
|  |  |  | Rectifier |  | Inverter |  | Comments
| Study case: SC01 | [6 empty] | both stations have shunt compensation active
| Shunt on? |  |  | YES |  | YES
|  |  | Xg | 16.93 | Ohm | 16.93 | Ohm | calculated using complete short circuit; Skss is around 10 GVA
|  |  | Xg_pu | 0.10581 | p.u. | 0.10581 | p.u.
|  |  | Xt | 0.06 | p.u. | 0.1 | p.u. | assume two different values for the built-in transformer (one small, one typical)
| Use Xc at value: |  |  | 2.4 | Ohm | 4 | Ohm | in this case the shunt is connected and hence we assume that the commutating voltage is located at the shunt (the grid reactance is ignored)
| EMT results |  | T_start | 5607 | us | 7431 | us | start of one commutation instance
|  |  | T_end | 5746 | us | 7648 | us | end of the same commutation instance
|  |  | dt | 0.000139 | s | 0.000217 | s
|  |  | ol | 0.043668 | rad | 0.068173 | rad | ol = overlap angle
|  |  | ol_deg | 2.502 | deg | 3.906 | deg | for the rectifier AND inverter: the load flow results are well matching the EMT simulation
| LDF results |  | ol_deg | 2.782 | deg | 4.187 | deg
| Study case: SC02 | [6 empty] | only the rectifier station has shunt compensation active
| Shunt on? |  |  | YES |  | NO
|  |  | Xg | 15.92 | Ohm | 16.93 | Ohm | calculated using complete short circuit; Skss is around 10 GVA
|  |  | Xg_pu | 0.0995 | p.u. | 0.10581 | p.u.
|  |  | Xt | 0.06 | p.u. | 0.1 | p.u. | assume two different values for the built-in transformer (one small, one typical)
| Use Xc at value: |  |  | 6.38 | Ohm | 8.2325 | Ohm | for the rectifier, the shunt is connected -> consider only the transformer for the inverter, the shunt is not connected -> consider both transformer and grid
| EMT results |  | T_start | 5433 | us | 7431 | us | start of one commutation instance
|  |  | T_end | 5829 | us | 8142 | us | end of the same commutation instance
|  |  | dt | 0.000396 | s | 0.000711 | s
|  |  | ol | 0.12441 | rad | 0.22337 | rad
|  |  | ol_deg | 7.128 | deg | 12.798 | deg | for the rectifier: the load flow results are well matching the EMT simulation for the inverter: the load flow results are deviating w.r.t. the EMT simulation; it is recommended to use an external transformer option. The load flow results are in the case of the inverter too optimistic (small overlap angle) by underestimating the effects of the grid reactance.
| LDF results |  | ol_deg | 7.422 | deg | 10.068 | deg
| Study case: SC03 | [6 empty] | neither rectifier nor inverter stations have shunt compensation
| Shunt on? |  |  | NO |  | NO
|  |  | Xg | 15.92 | Ohm | 15.92 | Ohm | calculated using complete short circuit; Skss is around 10 GVA
|  |  | Xg_pu | 0.0995 | p.u. | 0.0995 | p.u.
|  |  | Xt | 0.06 | p.u. | 0.1 | p.u. | assume two different values for the built-in transformer (one small, one typical)
| Use Xc at value: |  |  | 6.38 | Ohm | 7.98 | Ohm | for the rectifier, the shunt is not connected -> consider both transformer and grid for the inverter, the shunt is not connected -> consider both transformer and grid
| EMT results |  | T_start | 5076 | us | 7434 | us | start of one commutation instance
|  |  | T_end | 5746 | us | 8114 | us | end of the same commutation instance
|  |  | dt | 0.00067 | s | 0.00068 | s
|  |  | ol | 0.21049 | rad | 0.21363 | rad
|  |  | ol_deg | 12.06 | deg | 12.24 | deg | for the rectifier and inverter: the load flow results are slightly deviating w.r.t. to the EMT simulation; it is recommended to use an external transformer option. The load flow results are in this case too optimistic by underestimating the effects of the grid reactance.
| LDF results |  | ol_deg | 8.841 | deg | 9.758 | deg
Note on D15: Adrian Constantin:
Note on D27: Adrian Constantin:
Note on D40: Adrian Constantin: