{"text_format":"2","workbook":"xlsx","n_sheets":2,"sheets":["Cable System","Overhead Line"],"not_rendered":{"charts":4,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Cable System","index":0,"n_rows":1005,"n_cols":6,"rows_kept":1005,"cut":false,"hidden":false,"merged":[[0,0,0,1]]}
["Frequency Sweep Calculation",null,"EMT Time Domain Simulation",null,null,"EMT-FFT"]
[null,null,"FFT - Core_Send m U A(1)","FFT - Core_Send m U A(1)","FFT - Core m I bus1 A(2)"]
["Freq.Sweep","Core_Send","FFT - Core_Send m U A(1)","Core_Send","Core","hand calculation"]
["Frequency in Hz","Z, Magnitude A in Ohm","Frequency in Hz","FFT Mag, Phase Voltage A in V","FFT Mag, Phase Current A/Terminal i in A","Z (f)= U(f) / I(f)"]
[0,7182431092865.4297,0,1.136107,0.115468,{"$f":"D5/E5","v":9.839150240759345}]
[10,10080.137848,10,1002.272184,0.28717999999999999,{"$f":"D6/E6","v":3490.0486941987606}]
[20,5039.9443689999998,20,1002.272096,0.32825100000000001,3053.3710361887702]
[30,3359.840655,30,1002.2719509999999,0.38494400000000001,2603.6824862837188]
[40,2519.756453,40,1002.271749,0.45175399999999999,2218.6228544738951]
[50,2015.680773,50,1002.271489,0.52587099999999998,1905.926527608482]
[60,1679.6105230000001,60,1002.271168,0.60578200000000004,1654.5080045296822]
[70,1439.5444789999999,70,1002.270778,0.69054000000000004,1451.4304428418338]
[80,1259.481998,80,1002.271281,0.77947999999999995,1285.8203943654746]
[90,1119.4226490000001,90,1002.265491,0.87203299999999995,1149.3435351643802]
[100,1007.366093,100,1002.264876,0.96791199999999999,1035.491734785807]
[110,915.67567099999997,110,1002.264228,1.0667199999999999,939.57573496325199]
[120,839.26020900000003,120,1002.263538,1.168161,857.98407753725735]
[130,774.59498900000006,130,1002.2628110000001,1.2719769999999999,787.95670912288517]
[140,719.16230800000005,140,1002.262048,1.377937,727.36420315297437]
[150,671.115815,150,1002.261247,1.485832,674.54547149341249]
[160,629.07071399999995,160,1002.260401,1.595478,628.18816743320815]
[170,591.96802100000002,170,1002.259501,1.7067030000000001,587.2489243881331]
[180,558.98406299999999,180,1002.258538,1.8193509999999999,550.88794740542096]
[190,529.46856000000002,190,1002.257504,1.9332769999999999,518.42415960051255]
[200,502.901274,200,1002.2564,2.0483470000000001,489.30010393746761]
[210,478.86105400000002,210,1002.25523,2.1644320000000001,463.05692671333628]
[220,457.00331499999999,220,1002.254003,2.281412,439.31302325051331]
[230,437.04339399999998,230,1002.2527260000001,2.3991739999999999,417.74907780761214]
[240,418.74406800000003,240,1002.250212,2.5176099999999999,398.09589729942292]
[250,401.90606700000001,250,1002.249341,2.6366269999999998,380.12556990427544]
[260,386.36077699999998,260,1002.247973,2.756122,363.64427010125098]
[270,371.96455900000001,270,1002.246535,2.8760150000000002,348.48446026880941]
[280,358.59429499999999,280,1002.245017,2.9962300000000002,334.50202988422114]
[290,346.14384699999999,290,1002.24341,3.116695,321.57250228206482]
[300,334.52122700000001,300,1002.241716,3.2373419999999999,309.58783965364177]
[310,323.64631700000001,310,1002.239949,3.3581120000000002,298.45340149464937]
[320,313.44901199999998,320,1002.238131,3.478945,288.08679959010561]
[330,303.867706,330,1002.2362900000001,3.5997910000000002,278.41513298966521]
[340,294.84803900000003,340,1002.234446,3.7206000000000001,269.37441434177282]
[350,286.34186299999999,350,1002.232604,3.8413309999999998,260.90763956555685]
[360,278.30638299999998,360,1002.230747,3.9619439999999999,252.96438995604177]
[370,270.70342599999998,370,1002.228836,4.0824059999999998,245.49955002025769]
[380,263.49884100000003,380,1002.226801,4.2026880000000002,238.47280621354713]
[390,256.66197799999998,390,1002.224532,4.3227659999999997,231.84797233993237]
[400,250.16525300000001,400,1002.225914,4.4425819999999998,225.59536638828502]
[410,243.98377300000001,410,1001.647368,4.5580790000000002,219.75208591163076]
[420,238.09501499999999,420,1001.644437,4.6773600000000002,214.14739019446867]
[430,232.478554,430,1001.641057,4.7963659999999999,208.83332443770973]
[440,227.11582000000001,440,1001.637467,4.9150850000000004,203.7884323465413]
[450,221.98989499999999,450,1001.633765,5.0335089999999996,198.99314076919305]
[460,217.08533299999999,460,1001.630014,5.1516339999999996,194.42957593648927]
[470,212.388001,470,1001.626251,5.2694570000000001,190.08149245738224]
[480,207.88494800000001,480,1001.62249,5.3869740000000004,185.93416081087452]
[490,203.564277,490,1001.618724,5.5041890000000002,181.97389733528408]
[500,199.41504499999999,500,1001.614929,5.6211010000000003,178.18838853811732]
[510,195.427165,510,1001.61108,5.7377140000000004,174.56622620088766]
[520,191.59132500000001,520,1001.607154,5.8540320000000001,171.09697282146732]
[530,187.898912,530,1001.6031369999999,5.970059,167.77106172652563]
[540,184.341939,540,1001.59903,6.0857989999999997,164.57970925428197]
[550,180.91297800000001,550,1001.594833,6.2012590000000003,161.5147557939444]
[560,177.60508899999999,560,1001.589734,6.3164530000000001,158.56838228670426]
[570,174.41174899999999,570,1001.5859359999999,6.4313760000000002,155.73431502061143]
[580,171.32680500000001,580,1001.5816139999999,6.5460419999999999,153.00568099013114]
[590,168.34452999999999,590,1001.577253,6.6604619999999999,150.37654339894141]
[600,165.459844,600,1001.572847,6.7746449999999996,147.84137722345599]
[610,162.66842700000001,610,1001.568387,6.8886019999999997,145.3950144020514]
[620,159.96631500000001,620,1001.563868,7.0023400000000002,143.03273877018253]
[630,157.34943899999999,630,1001.559286,7.1158700000000001,140.7500819998117]
[640,154.81368000000001,640,1001.5546430000001,7.2291999999999996,138.5429429259116]
[650,152.35510300000001,650,1001.549943,7.3423410000000002,{"$f":"D70/E70","v":136.40744048798604}]
[660,149.97006099999999,660,1001.5451880000001,7.4553010000000004,134.34000692929769]
[670,147.655181,670,1001.540376,7.5680909999999999,132.33725334433743]
[680,145.40732299999999,680,1001.535499,7.6807220000000003,130.39600951577208]
[690,143.223555,690,1001.530542,7.7932040000000002,128.51332289004625]
[700,141.10111900000001,700,1001.525491,7.9055470000000003,126.6864254933909]
[710,139.037419,710,1001.520322,8.0177619999999994,124.91270282156043]
[720,137.03000599999999,720,1001.527552,8.1295380000000002,123.19612160002204]
[730,135.07656600000001,730,1001.518732,8.2415160000000007,121.52117789979415]
[740,133.17491100000001,740,1001.513402,8.3534009999999999,119.8928917694721]
[750,131.32297,750,1001.508003,8.4651929999999993,118.30893908738999]
[760,129.51881599999999,760,1001.502574,8.5769009999999994,116.76741680940471]
[770,127.760519,770,1001.497132,8.6885349999999999,115.26651293917789]
[780,126.046347,780,1001.49168,8.8001039999999993,113.80452776467187]
[790,124.374624,790,1001.486207,8.9116169999999997,112.37985283703284]
[800,122.743758,800,1001.480693,9.0230829999999997,110.99096539397898]
[810,121.152235,810,1001.475116,9.1345130000000001,109.63639944461187]
[820,119.59861600000001,820,1001.469458,9.2459140000000009,108.31481430608157]
[830,118.081529,830,1001.463709,9.3572939999999996,107.02492718514563]
[840,116.59967,840,1001.4578739999999,9.4686610000000009,105.76552207328997]
[850,115.151774,850,1001.451965,9.5800239999999999,104.53543383607389]
[860,113.736699,860,1001.445997,9.6913909999999994,103.3335665643869]
[870,112.353289,870,1001.439982,9.8027700000000006,102.15887774578002]
[880,111.000467,880,1001.434215,9.9141700000000004,101.01039370920611]
[890,109.677199,890,1001.427057,10.025586000000001,99.887134477725283]
[900,108.38249999999999,900,1001.420925,10.13705,98.788200216039186]
[910,107.115427,910,1001.414751,10.248559999999999,97.712727544162306]
[920,105.87508,920,1001.40851,10.360124000000001,96.659896155683072]
[930,104.660596,930,1001.402193,10.471748,95.628943037972263]
[940,103.471147,940,1001.395799,10.583439,94.619130794820094]
[950,102.305944,950,1001.3893389999999,10.695206000000001,93.629738314530812]
[960,101.16422799999999,960,1001.382828,10.807054000000001,92.660111442026661]
[970,100.045272,970,1001.376279,10.918991,91.709598350250488]
[980,98.948379000000003,980,1001.369702,11.031024,90.777583477290946]
[990,97.872878,990,1001.363097,11.14316,89.863476518330529]
[1000,96.818128999999999,1000,1001.356452,11.255407,88.966703025488101]
[1010,95.783513999999997,1010,1001.349752,11.367772,88.086720247380043]
[1020,94.768440999999996,1020,1001.34297,11.480259999999999,87.223021952464492]
[1030,93.772339000000002,1030,1001.3360699999999,11.592878000000001,86.375106336838869]
[1040,92.794659999999993,1040,1001.313391,11.705664000000001,85.540930527307125]
[1050,91.834879000000001,1050,1001.307398,11.818569,84.72323493648004]
[1060,90.892487000000003,1060,1001.300394,11.931611,83.919966381740068]
[1070,89.966997000000006,1070,1001.293318,12.044808,83.130699800279089]
[1080,89.057939000000005,1080,1001.286188,12.158163999999999,82.355048673467479]
[1090,88.164859000000007,1090,1001.279013,12.271687,81.592613387222144]
[1100,87.287321000000006,1100,1001.271794,12.385382999999999,80.843022294910057]
[1110,86.424905999999993,1110,1001.2645240000001,12.499257,80.105923416087862]
[1120,85.577207000000001,1120,1001.257195,12.613315,79.380971219699191]
[1130,84.743831999999998,1130,1001.2497969999999,12.727563999999999,78.667826537741234]
[1140,83.924404999999993,1140,1001.242326,12.842008,77.966181456980877]
[1150,83.118561999999997,1150,1001.234786,12.956654,77.275721494145017]
[1160,82.325948999999994,1160,1001.227184,13.071505999999999,76.596161452245823]
[1170,81.546228999999997,1170,1001.219531,13.186572,75.927203142712145]
[1180,80.779071000000002,1180,1001.2118369999999,13.301857,75.268576184513179]
[1190,80.024158999999997,1190,1001.204107,13.417369000000001,74.620002401364971]
[1200,79.281187000000003,1200,1001.197374,13.533104,73.981355201290114]
[1210,78.549858,1210,1001.183476,13.649046,73.351901370982262]
[1220,77.829884000000007,1220,1001.175527,13.765272,72.731982847850745]
[1230,77.120990000000006,1230,1001.167541,13.881748,72.121143605257785]
[1240,76.422905,1240,1001.159498,13.998481,71.519152542336556]
[1250,75.735370000000003,1250,1001.151393,14.115475999999999,70.925797543065499]
[1260,75.058133999999995,1260,1001.143231,14.23274,70.340864162487335]
[1270,74.390952999999996,1270,1001.1350200000001,14.350279,69.764150230110516]
[1280,73.733590000000007,1280,1001.126766,14.468099,69.195460025536178]
[1290,73.085817000000006,1290,1001.118471,14.586207,{"$f":"D134/E134","v":68.634599179896455}]
[1300,72.447412,1300,1001.11013,14.704609,68.081383870866617]
[1310,71.818160000000006,1310,1001.101733,14.823313000000001,67.535626684803859]
[1320,71.197852999999995,1320,1001.093269,14.942323,66.997164296341339]
[1330,70.586287999999996,1330,1001.084726,15.061647000000001,66.465820504225064]
[1340,69.983269000000007,1340,1001.076097,15.181290000000001,65.941438244049081]
[1350,69.388605999999996,1350,1001.067372,15.301259,65.423856429069005]
[1360,68.802114000000003,1360,1001.055673,15.421582000000001,64.91264469494763]
[1370,68.223613,1370,1001.047652,15.542223,64.408267208622604]
[1380,67.652929999999998,1380,1001.038813,15.663205,63.910215884935425]
[1390,67.089895999999996,1390,1001.029946,15.784538,63.418387411782341]
[1400,66.534345000000002,1400,1001.021046,15.906228,62.932647891127921]
[1410,65.986119000000002,1410,1001.0121,16.028282999999998,62.452859111609158]
[1420,65.445061999999993,1420,1001.003093,16.150708000000002,61.978898572124514]
[1430,64.911023999999998,1430,1000.994009,16.273510000000002,61.510639622306428]
[1440,64.383857000000006,1440,1000.984836,16.396695000000001,61.047963385304165]
[1450,63.863419999999998,1450,1000.975576,16.52027,60.590751603938678]
[1460,63.349572999999999,1460,1000.966241,16.64424,60.138897360287999]
[1470,62.842182000000001,1470,1000.956856,16.768612999999998,59.692286774105888]
[1480,62.341115000000002,1480,1000.947451,16.893395000000002,59.250816724524576]
[1490,61.846245000000003,1490,1000.938059,17.018595000000001,58.814376803725565]
[1500,61.357447999999998,1500,1000.928702,17.144219,58.382869584202119]
[1510,60.874602000000003,1510,1000.919402,17.270274000000001,57.956196989115512]
[1520,60.397590000000001,1520,1000.910065,17.396754000000001,57.534300076899399]
[1530,59.926296000000001,1530,1000.789408,17.524021000000001,57.109575935796919]
[1540,59.460610000000003,1540,1000.77963,17.651395999999998,56.696911111166507]
[1550,59.000422,1550,1000.7698360000001,17.779228,56.288711523357485]
[1560,58.545627000000003,1560,1000.759956,17.907523999999999,55.884887045244227]
[1570,58.096119999999999,1570,1000.749962,18.036292,55.485349316810797]
[1580,57.651800999999999,1580,1000.7398480000001,18.165537,55.090022827291044]
[1590,57.212572999999999,1590,1000.7296229999999,18.295269999999999,54.698816852661921]
[1600,56.778339000000003,1600,1000.719309,18.425495999999999,54.311661895017643]
[1610,56.349004999999998,1610,1000.708927,18.556224,53.928478498642825]
[1620,55.924481999999998,1620,1000.698499,18.687462,53.549192447856214]
[1630,55.50468,1630,1000.688036,18.819216999999998,53.173733848756839]
[1640,55.089511999999999,1640,1000.677541,18.951495999999999,52.80203425629302]
[1650,54.678894999999997,1650,1000.667007,19.084306999999999,52.434023776708273]
[1660,54.272745,1660,1000.656421,19.217656000000002,52.069639554376451]
[1670,53.870981999999998,1670,1000.645767,19.351552000000002,51.708812140752322]
[1680,53.473528000000002,1680,1000.634982,19.486008000000002,51.351461109941035]
[1690,53.080305000000003,1690,1000.623892,19.621015,50.997560116028652]
[1700,52.691240000000001,1700,1000.613011,19.756596999999999,50.647032532981264]
[1710,52.306258,1710,1000.60208,19.892759000000002,50.299814118292986]
[1720,51.925288999999999,1720,1000.591102,20.029506999999999,49.955852732670856]
[1730,51.548262999999999,1730,1000.5800850000001,20.16685,49.615090358682693]
[1740,51.175111000000001,1740,1000.569033,20.304794999999999,49.277475246610472]
[1750,50.805768,1750,1000.557942,20.443352000000001,48.942949375425322]
[1760,50.440167000000002,1760,1000.546804,20.582528,48.611463276036837]
[1770,50.078246,1770,1000.535607,20.722329999999999,48.282968517536396]
[1780,49.719942000000003,1780,1000.5243359999999,20.862769,47.957408529999057]
[1790,49.365195,1790,1000.512985,21.003851999999998,47.634737904266323]
[1800,49.013945,1800,1000.5015529999999,21.145589000000001,47.314905865237421]
[1810,48.666134,1810,1000.490048,21.287989,46.997865697882503]
[1820,48.321705999999999,1820,1000.478495,21.431059999999999,46.683574914166634]
[1830,47.980604,1830,1000.466949,21.574811,46.371991346760815]
[1840,47.642775999999998,1840,1000.437782,21.71932,46.062113454749046]
[1850,47.308166999999997,1850,1000.433665,21.864538,45.755993792322528]
[1860,46.976725000000002,1860,1000.421867,22.010383000000001,45.452269821929043]
[1870,46.648401,1870,1000.410093,22.156943999999999,45.151086404334457]
[1880,46.323143999999999,1880,1000.398306,22.30423,44.852402705675111]
[1890,46.000906000000001,1890,1000.386486,22.452252000000001,44.556175745755922]
[1900,45.681638999999997,1900,1000.374612,22.601019000000001,44.262367639264404]
[1910,45.365296999999998,1910,1000.362669,22.750541999999999,43.97093787919426]
[1920,45.051833999999999,1920,1000.35065,22.900829000000002,43.681853176581505]
[1930,44.741204000000003,1930,1000.338554,23.051891000000001,{"$f":"D198/E198","v":43.395075657784432}]
[1940,44.433365000000002,1940,1000.326388,23.203737,43.110572577167204]
[1950,44.128272000000003,1950,1000.314163,23.356377999999999,42.828308524549485]
[1960,43.825885,1960,1000.301889,23.509823999999998,42.548250850367914]
[1970,43.526161000000002,1970,1000.289575,23.664083999999999,42.270369518634233]
[1980,43.229058999999999,1980,1000.277223,23.819168999999999,41.994631424799081]
[1990,42.934539999999998,1990,1000.264831,23.975090000000002,41.72100421729386]
[2000,42.642564999999998,2000,1000.253027,24.131854000000001,41.449489417597171]
[2010,42.353093999999999,2010,1000.239295,24.289470999999999,41.179953857373015]
[2020,42.066090000000003,2020,1000.226691,24.447965,40.912472305977204]
[2030,41.781516000000003,2030,1000.214028,24.607337000000001,40.646983783738968]
[2040,41.499333,2040,1000.2013020000001,24.767600000000002,40.383456693422048]
[2050,41.219507,2050,1000.188519,24.928764000000001,40.121865608740165]
[2060,40.942,2060,1000.175689,25.09084,39.862184327029304]
[2070,40.666777000000003,2070,1000.162818,25.25384,39.60438563006656]
[2080,40.393802999999998,2080,1000.14991,25.417774999999999,39.348444543237953]
[2090,40.123041000000001,2090,1000.136961,25.582656,39.09433645200874]
[2100,39.854455999999999,2100,1000.123962,25.748495999999999,38.84203419104557]
[2110,39.588012999999997,2110,1000.110898,25.915306999999999,38.591512653120418]
[2120,39.323675000000001,2120,1000.097753,26.083102,38.342745927995836]
[2130,39.061407000000003,2130,1000.084509,26.251891000000001,38.095713143102721]
[2140,38.801170999999997,2140,1000.071147,26.421689000000001,37.850386740983893]
[2150,38.542929999999998,2150,1000.05761,26.592507999999999,37.606742846519026]
[2160,38.286644000000003,2160,999.98585400000002,26.764890999999999,37.361850418146673]
[2170,38.032274000000001,2170,999.97486600000002,26.937792000000002,37.121634393791439]
[2180,37.779775999999998,2180,999.96144800000002,27.111737999999999,36.882971058513476]
[2190,37.529107000000003,2190,999.94797400000004,27.286756,36.64590887975104]
[2200,37.28022,2200,999.93445299999996,27.462859000000002,36.410428098545744]
[2210,37.033062999999999,2210,999.92088799999999,27.640062,36.176506695245472]
[2220,36.787584000000003,2220,999.90728100000001,27.818377999999999,35.944125894040262]
[2230,36.543723,2230,999.89362600000004,27.997820999999998,35.713265900228457]
[2240,36.301416000000003,2240,999.87991899999997,28.178405000000001,35.483907588098049]
[2250,36.060594000000002,2250,999.86615500000005,28.360143999999998,35.256032374165663]
[2260,35.821181000000003,2260,999.85233300000004,28.543053,35.029621148095124]
[2270,35.583092999999998,2270,999.83845199999996,28.727146999999999,34.804655401387407]
[2280,35.346240000000002,2280,999.82451600000002,28.91244,34.581118577332113]
[2290,35.110522000000003,2290,999.81052699999998,29.098949000000001,34.358991006857323]
[2300,34.875833,2300,999.79648899999995,29.286688000000002,34.138257251895467]
[2310,34.642060999999998,2310,999.78241000000003,29.475674000000001,33.918899021613548]
[2320,34.409089000000002,2320,999.76820999999995,29.665918999999999,33.700901360918564]
[2330,34.1768,2330,999.75396699999999,29.857458000000001,33.484229199953994]
[2340,33.945084000000001,2340,999.73971200000005,30.050280999999998,33.26889728585234]
[2350,33.713839,2350,999.72539800000004,30.244416000000001,33.054875253666658]
[2360,33.482989000000003,2360,999.71102599999995,30.439878,32.842149564462773]
[2370,33.252490000000002,2370,999.696595,30.636685,32.63070384410063]
[2380,33.02234,2380,999.68210599999998,30.834855000000001,32.420522360166764]
[2390,32.792597000000001,2390,999.66755899999998,31.034406000000001,32.211589904443471]
[2400,32.563383000000002,2400,999.65295100000003,31.235354999999998,32.003892736291938]
[2410,32.334885999999997,2410,999.638283,31.437721,31.79741569053304]
[2420,32.10736,2420,999.62355200000002,31.641522999999999,31.592144031752202]
[2430,31.881107,2430,999.60875799999997,31.846779000000002,31.388064645407308]
[2440,31.656459999999999,2440,999.59390099999996,32.053508999999998,31.18516294113072]
[2450,31.433751000000001,2450,999.57898299999999,32.261730999999997,30.983426865719018]
[2460,31.213284000000002,2460,999.56400699999995,32.471465999999999,30.782841988101183]
[2470,30.995311000000001,2470,999.54897400000004,32.682732999999999,30.583396253917936]
[2480,30.780010999999998,2480,999.53398500000003,32.895574000000003,30.385059856380678]
[2490,30.567482999999999,2490,999.51891699999999,33.109965000000003,30.18785785487843]
[2500,30.357747,2500,999.50371900000005,33.325952999999998,29.991752043820025]
[2510,30.150756000000001,2510,999.48847999999998,33.543557999999997,29.796734144899002]
[2520,29.946407000000001,2520,999.47319000000005,33.762802000000001,29.602791557406878]
[2530,29.74456,2530,999.45784300000003,33.983705999999998,29.409913180157577]
[2540,29.545051999999998,2540,999.44243700000004,34.206294,29.218085917170683]
[2550,29.347712999999999,2550,999.42697099999998,34.430588999999998,29.027298109829026]
[2560,29.152373000000001,2560,999.41144799999995,34.656613,28.837539548368444]
[2570,28.958872,2570,999.39587100000006,34.884390000000003,{"$f":"D262/E262","v":28.648798818038667}]
[2580,28.767061999999999,2580,999.38024499999995,35.113945999999999,28.461063447554427]
[2590,28.576809999999998,2590,999.36457499999995,35.345305000000003,28.274323138532822]
[2600,28.388000000000002,2600,999.34886100000006,35.578491999999997,28.088567132075191]
[2610,28.200529,2610,999.33310200000005,35.813533,27.90378435995131]
[2620,28.014309999999998,2620,999.31729099999995,36.050454000000002,27.719964109189856]
[2630,27.829266000000001,2630,999.301422,36.289279999999998,27.537096960865579]
[2640,27.645332,2640,999.28327100000001,36.530050000000003,27.355102744179106]
[2650,27.462451000000001,2650,999.31044799999995,36.773161999999999,27.174993763114522]
[2660,27.280574000000001,2660,999.29463599999997,37.017878000000003,26.994919481878455]
[2670,27.099656,2670,999.27867000000003,37.264609,26.815756204499557]
[2680,26.919658999999999,2680,999.26260000000002,37.513385999999997,26.637494146756044]
[2690,26.740545000000001,2690,999.246443,37.764237999999999,26.460124602540638]
[2700,26.562282,2700,999.23021000000006,38.017195999999998,26.28363780432413]
[2710,26.384837999999998,2710,999.21391200000005,38.272289999999998,26.108025205703658]
[2720,26.208179999999999,2720,999.19755799999996,38.529552000000002,25.933277345140166]
[2730,26.03228,2730,999.18115599999999,38.789014000000002,25.75938527336632]
[2740,25.857105000000001,2740,999.16470800000002,39.050708,25.58634040642746]
[2750,25.682624000000001,2750,999.14821600000005,39.314666000000003,25.41413466414798]
[2760,25.508807000000001,2760,999.13167699999997,39.580922999999999,25.242758411672209]
[2770,25.335619999999999,2770,999.11508600000002,39.849511999999997,25.072203795117996]
[2780,25.163032000000001,2780,999.09844099999998,40.120469,24.902461658661068]
[2790,24.991008999999998,2790,999.08174499999996,40.393828999999997,24.733524147958345]
[2800,24.819517999999999,2800,999.06624499999998,40.669623999999999,24.565416316610158]
[2810,24.648527000000001,2810,999.04875400000003,40.947896999999998,24.398047938823332]
[2820,24.478007000000002,2820,999.03184299999998,41.228690999999998,24.231471307202067]
[2830,24.307929000000001,2830,999.01488500000005,41.512037999999997,24.065667048194552]
[2840,24.138269000000001,2840,998.997882,41.797978000000001,23.900627011191784]
[2850,23.969009,2850,998.98083399999996,42.086551999999998,23.736343000966201]
[2860,23.800135000000001,2860,998.96374000000003,42.377800999999998,23.572807376201517]
[2870,23.631643,2870,998.94659200000001,42.671765999999998,23.410012887678473]
[2880,23.463536000000001,2880,998.92938200000003,42.968490000000003,23.247951743242549]
[2890,23.295828,2890,998.912104,43.268016000000003,23.086616774848192]
[2900,23.128540999999998,2900,998.89475200000004,43.570390000000003,22.925999790224505]
[2910,22.961708999999999,2910,998.87733100000003,43.875658000000001,22.76609346804554]
[2920,22.795373000000001,2920,998.85984900000005,44.183864,22.606892167692713]
[2930,22.629583,2930,998.84232499999996,44.495058,22.448387976030954]
[2940,22.464395,2940,998.82478200000003,44.809286999999998,22.290575210446889]
[2950,22.299868,2950,998.80725700000005,45.126600000000003,22.133448055027412]
[2960,22.136063,2960,998.78312300000005,45.447125999999997,21.976815937711883]
[2970,21.973037000000001,2970,998.78651500000001,45.770890999999999,21.821434828524531]
[2980,21.810845,2980,998.76876000000004,46.097763999999998,21.666316830464925]
[2990,21.649535,2990,998.75102600000002,46.427928000000001,21.511858681266155]
[3000,21.489146000000002,3000,998.733249,46.761437999999998,21.358052526100675]
[3010,21.329711,3010,998.71539800000005,47.098351000000001,21.204890973783776]
[3020,21.171249,3020,998.69745899999998,47.438723000000003,21.052368104428105]
[3030,21.013774999999999,3030,998.67942700000003,47.782612,20.900477918620272]
[3040,20.857291,3040,998.66131099999996,48.130077999999997,20.749214472496803]
[3050,20.701792999999999,3050,998.64313100000004,48.481181999999997,20.598572266658021]
[3060,20.547270999999999,3060,998.62490600000001,48.835985000000001,20.448546415107629]
[3070,20.393708,3070,998.60665200000005,49.19455,20.299131753415775]
[3080,20.241084000000001,3080,998.58837700000004,49.556941999999999,20.15032277415342]
[3090,20.089375,3090,998.57007499999997,49.923226999999997,20.002113945879341]
[3100,19.938555999999998,3100,998.55173400000001,50.293472000000001,19.854499884199683]
[3110,19.788598,3110,998.53333999999995,50.667748000000003,19.707474269430723]
[3120,19.639475999999998,3120,998.51516800000002,51.046118999999997,19.561039851041372]
[3130,19.491161999999999,3130,998.49663899999996,51.428671999999999,19.415174457547728]
[3140,19.343629,3140,998.47797600000001,51.815468000000003,19.269882421982562]
[3150,19.196853000000001,3150,998.45923500000004,52.206586999999999,19.125158191245102]
[3160,19.050806999999999,3160,998.44044599999995,52.602103,18.980998649426621]
[3170,18.905470999999999,3170,998.42163400000004,53.002097999999997,18.837398361098838]
[3180,18.760821,3180,998.40281500000003,53.406649000000002,18.694354236679406]
[3190,18.616838000000001,3190,998.38398400000005,53.815840999999999,18.551860668683037]
[3200,18.473502,3200,998.36512200000004,54.229757999999997,18.409912911652679]
[3210,18.330798000000001,3210,998.34618999999998,54.648485000000001,{"$f":"D326/E326","v":18.2685062541075}]
[3220,18.188707000000001,3220,998.32714299999998,55.072113000000002,18.127634634247645]
[3230,18.047215999999999,3230,998.30794400000002,55.500729999999997,17.987293932890612]
[3240,17.906310000000001,3240,998.28857100000005,55.934432000000001,17.847478472651694]
[3250,17.765975999999998,3250,998.26903600000003,56.373311000000001,17.708185279378039]
[3260,17.626203,3260,998.24938999999995,56.817466000000003,17.569410610462633]
[3270,17.486979999999999,3270,998.22976500000004,57.266995999999999,17.431152927944748]
[3280,17.348296999999999,3280,998.54299900000001,57.726019000000001,17.297970937507401]
[3290,17.210142999999999,3290,998.52228500000001,58.186593999999999,17.160693148665825]
[3300,17.072510000000001,3300,998.50167399999998,58.652859999999997,17.023921322847684]
[3310,16.935390999999999,3310,998.48120300000005,59.124918999999998,16.88765447611015]
[3320,16.798776,3320,998.46083799999997,59.602882999999999,16.751888293725656]
[3330,16.662659000000001,3330,998.44053299999996,60.086863999999998,16.616619116617567]
[3340,16.527032999999999,3340,998.42023400000005,60.576979999999999,16.481842343411639]
[3350,16.391891999999999,3350,998.39988800000003,61.073352,16.347553479625617]
[3360,16.257228999999999,3360,998.37945200000001,61.576101000000001,16.213749097234981]
[3370,16.123038000000001,3370,998.35890700000004,62.085354000000002,16.080425457508063]
[3380,15.989315,3380,998.33825400000001,62.601239999999997,15.94757953676317]
[3390,15.856052999999999,3390,998.31750999999997,63.123891,15.815208698082316]
[3400,15.723247000000001,3400,998.29670399999998,63.653441999999998,15.683310636995875]
[3410,15.590894,3410,998.27586099999996,64.190032000000002,15.551882899824694]
[3420,15.458988,3420,998.254999,64.733801999999997,15.420923353150183]
[3430,15.327525,3430,998.23412199999996,65.284898999999996,15.29042913890393]
[3440,15.1965,3440,998.21246699999995,65.843473000000003,15.160386011229996]
[3450,15.065910000000001,3450,998.19425799999999,66.409695999999997,15.030851187754271]
[3460,14.935750000000001,3460,998.17327499999999,66.983682000000002,14.901737933725411]
[3470,14.806016,3470,998.15218900000002,67.565613999999997,14.773079528293787]
[3480,14.676705999999999,3480,998.13100899999995,68.155658000000003,14.644873782892683]
[3490,14.547815,3490,998.10974599999997,68.753983000000005,14.51711889913345]
[3500,14.41934,3500,998.08841500000005,69.360763000000006,14.38981308495698]
[3510,14.291276999999999,3510,998.06703200000004,69.976177000000007,14.262954548088558]
[3520,14.163624,3520,998.04561100000001,70.600407000000004,14.136541889907235]
[3530,14.036376000000001,3530,998.02415599999995,71.233641000000006,14.010573403091945]
[3540,13.909532,3540,998.00266499999998,71.876070999999996,13.885047570282467]
[3550,13.783087999999999,3550,997.98112600000002,72.527895999999998,13.759962456376785]
[3560,13.657041,3560,997.95952899999997,73.189317000000003,13.635316872816288]
[3570,13.531388,3570,997.93786699999998,73.860543000000007,13.511109267095422]
[3580,13.406127,3580,997.91614300000003,74.541786999999999,13.387338607806653]
[3590,13.281255,3590,997.89438199999995,75.233269000000007,13.264004013968872]
[3600,13.15677,3600,997.879278,75.935186999999999,13.141197347680199]
[3610,13.032669,3610,997.85624900000005,76.647816000000006,13.018717310875498]
[3620,12.908951,3620,997.83427400000005,77.371382999999994,12.896683958718951]
[3630,12.785612,3630,997.81226700000002,78.106122999999997,12.775083804889407]
[3640,12.662649999999999,3640,997.79022499999996,78.852283,12.653916754699416]
[3650,12.540063999999999,3650,997.76813400000003,79.610119999999995,12.533182138150277]
[3660,12.417852,3660,997.74598000000003,80.379895000000005,12.41287986255767]
[3670,12.296011999999999,3670,997.72375499999998,81.161877000000004,12.293009869646065]
[3680,12.174541,3680,997.70145500000001,81.956343000000004,12.173572154140651]
[3690,12.053438999999999,3690,997.67908399999999,82.763576,12.054567144367953]
[3700,11.932703999999999,3700,997.65665200000001,83.583864000000005,11.935995828094283]
[3710,11.812334,3710,997.63417200000004,84.417507999999998,11.81785858923957]
[3720,11.692329000000001,3720,997.61165100000005,85.264809999999997,11.700156852516297]
[3730,11.572685999999999,3730,997.58909000000006,86.126085000000003,11.582891408566871]
[3740,11.453405,3740,997.56647999999996,87.001652000000007,11.466063655894716]
[3750,11.334485000000001,3750,997.54380300000003,87.891841999999997,11.349674557964095]
[3760,11.215925,3760,997.52017899999998,88.797003000000004,11.233714486963034]
[3770,11.097723999999999,3770,997.51034100000004,89.717545000000001,11.118341914059284]
[3780,10.979882,3780,997.48754599999995,90.653660000000002,11.003279360149385]
[3790,10.862397,3790,997.46463600000004,91.605797999999993,10.888662702332445]
[3800,10.745271000000001,3800,997.44164699999999,92.574329000000006,10.774495022264757]
[3810,10.628501999999999,3810,997.41860399999996,93.559635999999998,10.660779013719122]
[3820,10.512091,3820,997.39552300000003,94.562106999999997,10.547517971442833]
[3830,10.396037,3830,997.37241600000004,95.582142000000005,10.434715053780653]
[3840,10.280341999999999,3840,997.34928300000001,96.620148999999998,10.322373680048869]
[3850,10.165004,3850,997.32611399999996,97.676542999999995,{"$f":"D390/E390","v":10.210497662678335}]
[3860,10.050026000000001,3860,997.30289400000004,98.751751999999996,10.099090636893207]
[3870,9.9354080000000007,3870,997.27960800000005,99.846209999999999,9.988156866444907]
[3880,9.8211499999999994,3880,997.25624600000003,100.960362,9.8777007752805002]
[3890,9.707255,3890,997.23280799999998,102.09465899999999,9.7677274968909007]
[3900,9.5937230000000007,3900,997.20930499999997,103.24956299999999,9.6582423791953484]
[3910,9.480556,3910,997.18575999999996,104.425545,9.5492511913631866]
[3920,9.367756,3920,997.16330600000003,105.62306700000001,9.4407721184615863]
[3930,9.2553249999999991,3930,997.13937899999996,106.842642,9.3327847415079823]
[3940,9.1432660000000006,3940,997.115724,108.08475,9.2253136913394354]
[3950,9.0315799999999999,3950,997.09202200000004,109.34988800000001,9.1183634499927422]
[3960,8.9202720000000006,3960,997.068264,110.638561,9.0119417225609073]
[3970,8.8093430000000001,3970,997.04443300000003,111.951278,8.9060567312148056]
[3980,8.698798,3980,997.02051600000004,113.288552,8.8007172692965483]
[3990,8.5886410000000009,3990,996.99650799999995,114.650901,8.6959326032684192]
[4000,8.4788750000000004,4000,996.97241899999995,116.038844,8.5917127802479651]
[4010,8.3695050000000002,4010,996.94826599999999,117.4529,8.488068544923113]
[4020,8.2605360000000001,4020,996.92407300000002,118.89358900000001,8.3850111800393208]
[4030,8.1519739999999992,4030,996.89986199999998,120.36142700000001,8.2825526985485141]
[4040,8.0438229999999997,4040,996.87564399999997,121.856925,8.1807057251772921]
[4050,7.9360910000000002,4050,996.85141899999996,123.380589,8.0794833861589037]
[4060,7.8287829999999996,4060,996.82716900000003,124.93291499999999,7.9788994677663618]
[4070,7.721908,4070,996.80285400000002,126.51438899999999,7.8789682492163013]
[4080,7.6154710000000003,4080,996.78174100000001,128.12550100000001,7.7797295091162209]
[4090,7.5094830000000004,4090,996.738834,129.766548,7.681015249014715]
[4100,7.4039520000000003,4100,996.71436700000004,131.43821500000001,7.5831398577651097]
[4110,7.2988860000000004,4110,996.68977299999995,133.140784,7.485983956651479]
[4120,7.1942959999999996,4120,996.665076,134.87463099999999,7.3895666561638267]
[4130,7.0901940000000003,4130,996.64029300000004,136.64009300000001,7.2939081869623728]
[4140,6.9865899999999996,4140,996.61544000000004,138.437467,7.1990297250960253]
[4150,6.8834960000000001,4150,996.59052699999995,140.26700199999999,7.1049535014657259]
[4160,6.7809270000000001,4160,996.565561,142.12889300000001,7.0117028280801428]
[4170,6.6788959999999999,4170,996.54054199999996,144.02327199999999,6.9193021944397985]
[4180,6.5774169999999996,4180,996.51546800000006,145.95020400000001,6.8277771506232359]
[4190,6.4765079999999999,4190,996.49033699999995,147.909671,6.7371547124866495]
[4200,6.3761850000000004,4200,996.465149,149.90157099999999,6.6474630142468625]
[4210,6.2764670000000002,4210,996.43990699999995,151.92570000000001,6.55873171556886]
[4220,6.1773720000000001,4220,996.41461600000002,153.98174399999999,6.4709918858952529]
[4230,6.0789220000000004,4230,996.38927999999999,156.06926899999999,6.3842759460864782]
[4240,5.9811389999999998,4240,996.36341200000004,158.18769800000001,6.2986150288374505]
[4250,5.8840459999999997,4250,996.33880899999997,160.33632499999999,6.2140554175730296]
[4260,5.787668,4260,996.31334200000003,162.51424900000001,6.1306214570760496]
[4270,5.6920330000000003,4270,996.28779299999997,164.72040899999999,6.0483567218437395]
[4280,5.5971690000000001,4280,996.262159,166.95354499999999,5.9673016167461439]
[4290,5.5031049999999997,4290,996.23644400000001,169.21218200000001,5.8874983598994071]
[4300,5.4098759999999997,4300,996.21065499999997,171.49461199999999,5.808990984509764]
[4310,5.3175140000000001,4310,996.18480999999997,173.798878,5.7318253228309102]
[4320,5.2260580000000001,4320,996.15892699999995,176.12275600000001,5.6560489378215264]
[4330,5.1355459999999997,4330,996.13302499999998,178.46373199999999,5.5817112745350412]
[4340,5.0460190000000003,4340,996.10710800000004,180.818985,5.5088635078888428]
[4350,4.957522,4350,996.08116800000005,183.185374,5.4375583937176124]
[4360,4.8701020000000002,4360,996.05517799999996,185.55941100000001,5.3678505047636733]
[4370,4.7838099999999999,4370,996.02909199999999,187.937254,5.299795920185149]
[4380,4.6986970000000001,4380,996.00284099999999,190.31469000000001,5.2334522416530218]
[4390,4.6148220000000002,4390,995.97626000000002,192.68711999999999,5.1688782311967714]
[4400,4.5322430000000002,4400,996.20957699999997,195.049273,5.1074764939011077]
[4410,4.4510230000000002,4410,996.17857200000003,197.39635100000001,5.0465906130149287]
[4420,4.3712309999999999,4420,996.15173500000003,199.72229200000001,4.9876842741219889]
[4430,4.2929370000000002,4430,996.12471000000005,202.02089100000001,4.9308004982514406]
[4440,4.2162160000000002,4440,996.09758099999999,204.28558899999999,4.8760051351444087]
[4450,4.141146,4450,996.07039399999996,206.50946500000001,4.8233643625002847]
[4460,4.0678109999999998,4460,996.04317900000001,208.68525600000001,4.7729446636134174]
[4470,3.9962979999999999,4470,996.01594499999999,210.80539400000001,4.7248124258148723]
[4480,3.9266969999999999,4480,995.98868900000002,212.86204699999999,4.6790336888942914]
[4490,3.859105,4490,995.96139400000004,214.84716900000001,{"$f":"D454/E454","v":4.635673807738188}]
[4500,3.7936190000000001,4500,995.93404399999997,216.75256200000001,4.5947971032517714]
[4510,3.7303440000000001,4510,995.90662199999997,218.569942,4.5564665154186663]
[4520,3.6693850000000001,4520,995.87911999999994,220.29101800000001,4.5207431925345221]
[4530,3.6108500000000001,4530,995.851539,221.90757400000001,4.4876861165631059]
[4540,3.554853,4540,995.82388400000002,223.41156699999999,4.4573515032012647]
[4550,3.5015070000000001,4550,995.79616099999998,224.79521600000001,4.4297924961178889]
[4560,3.4509259999999999,4560,995.76793499999997,226.051109,4.4050566237213191]
[4570,3.4032269999999998,4570,995.74125800000002,227.17230799999999,4.3831982285446518]
[4580,3.3585229999999999,4580,995.71342000000004,228.152402,4.3642469299972575]
[4590,3.3169300000000002,4590,995.68552399999999,228.98568399999999,4.3482435522039014]
[4600,3.2785579999999999,4600,995.65756799999997,229.66718700000001,4.3352190663614474]
[4610,3.2435139999999998,4610,995.629547,230.19277299999999,4.3251989800739752]
[4620,3.2119,4620,995.60146099999997,230.55920499999999,4.3182030446366264]
[4630,3.1838120000000001,4630,995.57331199999999,230.76420100000001,4.3142450505137058]
[4640,3.159338,4640,995.54510700000003,230.80647500000001,4.3133326610529448]
[4650,3.138557,4650,995.51685299999997,230.68575799999999,4.3154673337050999]
[4660,3.1215380000000001,4660,995.48855600000002,230.40280200000001,4.320644312303112]
[4670,3.1083400000000001,4670,995.46021800000005,229.95936699999999,4.3288526620444214]
[4680,3.0990090000000001,4680,995.43184099999996,229.358194,4.3400753364843814]
[4690,3.0935800000000002,4690,995.40342199999998,228.60295500000001,4.3542893922784156]
[4700,3.0920740000000002,4700,995.37496199999998,227.69819100000001,4.3714662713328272]
[4710,3.0945010000000002,4710,995.34647299999995,226.64923999999999,4.3915720741000497]
[4720,3.1008580000000001,4720,995.32381699999996,225.46211299999999,4.4145945576230803]
[4730,3.111132,4730,995.294175,224.14354399999999,4.4404320429590429]
[4740,3.125299,4740,995.265488,222.70069799999999,4.4690721535143103]
[4750,3.1433219999999999,4750,995.23674000000005,221.14117200000001,4.5004588290777443]
[4760,3.165162,4760,995.20793600000002,219.47288800000001,4.534537022176516]
[4770,3.190766,4770,995.17907400000001,217.70398800000001,4.5712487085904918]
[4780,3.2200790000000001,4780,995.15015200000005,215.84273899999999,4.6105333754127358]
[4790,3.2530380000000001,4790,995.12116900000001,213.897446,4.6523284293913445]
[4800,3.2895750000000001,4800,995.092127,211.87636599999999,4.6965697297262503]
[4810,3.3296160000000001,4810,995.06302900000003,209.78763699999999,4.7431919403334533]
[4820,3.3730799999999999,4820,995.03388199999995,207.63921500000001,4.792128895305253]
[4830,3.41988,4830,995.00468899999998,205.438816,4.8433139772378748]
[4840,3.4699170000000001,4840,994.97545300000002,203.19387,4.8966804608820134]
[4850,3.523085,4850,994.94617100000005,200.911483,4.9521617985369213]
[4860,3.5792660000000001,4860,994.91683399999999,198.59841,5.0096918399296344]
[4870,3.638331,4870,994.887429,196.26102900000001,5.0692052012017115]
[4880,3.700142,4880,994.85886700000003,193.90534,5.1306419255911164]
[4890,3.7645520000000001,4890,994.82459600000004,191.53698700000001,5.193903337322519]
[4900,3.83141,4900,994.79495699999995,189.16104300000001,5.2589843089414554]
[4910,3.90056,4910,994.76528399999995,186.782374,5.3257984824628037]
[4920,3.9718499999999999,4920,994.73557600000004,184.40539000000001,5.3942868806600499]
[4930,4.0451329999999999,4930,994.70584199999996,182.03412499999999,5.4643921407593217]
[4940,4.1202680000000003,4940,994.67608600000005,179.672247,5.5360585878352158]
[4950,4.1971230000000004,4950,994.64630299999999,177.323072,5.6092323000133906]
[4960,4.2755780000000003,4960,994.61648300000002,174.98958400000001,5.683861063410494]
[4970,4.3555250000000001,4970,994.58660799999996,172.67445000000001,5.7598944603558886]
[4980,4.4368639999999999,4980,994.55666099999996,170.38004100000001,5.8372838459406164]
[4990,4.5195080000000001,4990,994.52663399999994,168.10844599999999,5.9159825556890819]
[5000,4.6033799999999996,5000,994.49652800000001,165.86149900000001,5.9959456172526204]
[5010,4.6884100000000002,5010,994.46635400000002,163.64078799999999,6.0771300734631035]
[5020,4.7745369999999996,5020,994.43613000000005,161.44768300000001,6.1594945899595226]
[5030,4.8617049999999997,5030,994.40587100000005,159.283345,6.2429996745736354]
[5040,4.949865,5040,994.37429599999996,157.14873499999999,6.3275997480985131]
[5050,5.0389710000000001,5050,994.34447899999998,155.04468,6.4132769921547776]
[5060,5.128984,5060,994.31417599999997,152.97182000000001,6.4999826503992688]
[5070,5.2198640000000003,5070,994.28380000000004,150.93065300000001,6.5876863330075173]
[5080,5.3115779999999999,5080,994.25332800000001,148.92155199999999,6.6763562066557034]
[5090,5.4040939999999997,5090,994.22274500000003,146.94477499999999,6.7659618724109114]
[5100,5.4973809999999999,5100,994.19205299999999,145.00047499999999,6.8564744563767812]
[5110,5.591412,5110,994.16127700000004,143.08871199999999,6.9478665584745789]
[5120,5.6861610000000002,5120,994.13045799999998,141.20946000000001,7.0401123125886889]
[5130,5.7816020000000004,5130,994.09964300000001,139.36262199999999,{"$f":"D518/E518","v":7.1331869961516663}]
[5140,5.877713,5140,994.06886799999995,137.548034,7.2270670768002399]
[5150,5.9744719999999996,5150,994.03814299999999,135.76547400000001,7.3217299930024913]
[5160,6.0718579999999998,5160,994.00743899999998,134.01467099999999,7.41715389503885]
[5170,6.1698519999999997,5170,993.97668299999998,132.29530800000001,7.5133177285471069]
[5180,6.2684340000000001,5180,993.94575499999996,130.60702900000001,7.6102010941539744]
[5190,6.3675879999999996,5190,993.91446099999996,128.94944699999999,7.7077838185688385]
[5200,6.4672980000000004,5200,993.88612699999999,127.322175,7.8060724850168475]
[5210,6.5675460000000001,5210,991.65727800000002,125.73207499999999,7.8870668284127188]
[5220,6.6683199999999996,5220,991.622884,124.164294,7.9863771786114288]
[5230,6.7696040000000002,5230,991.58769299999994,122.625416,8.0863146103414643]
[5240,6.8713860000000002,5240,991.55215499999997,121.114948,8.1868685193176987]
[5250,6.9736529999999997,5250,991.51644999999996,119.63239,8.2880267626518194]
[5260,7.0763939999999996,5260,991.48069599999997,118.177235,8.3897774050983678]
[5270,7.1795980000000004,5270,991.44496400000003,116.74897,8.492108872566499]
[5280,7.2832530000000002,5280,991.40928299999996,115.347078,8.5950099490166529]
[5290,7.3873509999999998,5290,991.37364100000002,113.97104299999999,8.6984694963263607]
[5300,7.4918820000000004,5300,991.33799899999997,112.620346,8.8024769431981671]
[5310,7.5968369999999998,5310,991.30230800000004,111.294471,8.9070220568279623]
[5320,7.7022089999999999,5320,991.266524,109.99290499999999,9.0120951346816423]
[5330,7.8079890000000001,5330,991.23062200000004,108.715137,9.1176872821307313]
[5340,7.9141709999999996,5340,991.19460000000004,107.460662,9.2237901903116892]
[5350,8.0207479999999993,5350,991.15846799999997,106.228979,9.3303962565619685]
[5360,8.127713,5360,991.12138800000002,105.019587,9.4374908177843047]
[5370,8.235061,5370,991.08565699999997,103.832016,9.545087297544141]
[5380,8.3427860000000003,5380,991.04942100000005,102.665774,9.6531627083432898]
[5390,8.4508829999999993,5390,991.01316799999995,101.520391,9.7617154370494887]
[5400,8.559348,5400,990.97688400000004,100.395402,9.8707397376624879]
[5410,8.6681760000000008,5410,990.94055000000003,99.290351999999999,9.9802300026089146]
[5420,8.7773629999999994,5420,990.90414799999996,98.204791999999998,10.090181220484638]
[5430,8.8869050000000005,5430,990.86766699999998,97.138283999999999,10.200588544471302]
[5440,8.9968000000000004,5440,990.83110699999997,96.090397999999993,10.311447632884194]
[5450,9.1070430000000009,5450,990.79447600000003,95.060713000000007,10.42275451899882]
[5460,9.2176329999999993,5460,990.75778600000001,94.048815000000005,10.534505788297279]
[5470,9.3285669999999996,5470,990.721045,93.054300999999995,10.646698049991263]
[5480,9.4398420000000005,5480,990.68425400000001,92.076775999999995,10.75932821540146]
[5490,9.5514569999999992,5490,990.64740099999995,91.115854999999996,10.872393185576758]
[5500,9.663411,5500,990.61046699999997,90.17116,10.985890244730133]
[5510,9.7757009999999998,5510,990.57342500000004,89.242322999999999,11.099816675547544]
[5520,9.8883279999999996,5520,990.54507999999998,88.329066999999995,11.214259514368017]
[5530,10.001289999999999,5530,990.50403500000004,87.430854999999994,11.328998612675127]
[5540,10.114587,5540,990.46680000000003,86.547471000000002,11.444202685021265]
[5550,10.228218,5550,990.429484,85.678556999999998,11.559829188066274]
[5560,10.342185000000001,5560,990.39213199999995,84.823786999999996,11.675877333795531]
[5570,10.456486999999999,5570,990.35476800000004,83.982842000000005,11.792346441431453]
[5580,10.571126,5580,990.31740000000002,83.155411000000001,11.909235828321503]
[5590,10.686102,5590,990.28002000000004,82.341193000000004,12.026544478169026]
[5600,10.801418,5600,990.24260700000002,81.53989,12.144272048932125]
[5610,10.917076,5610,990.20513400000004,80.751215999999999,12.262417621054771]
[5620,11.033078,5620,990.16757500000006,79.974889000000005,12.380980922649359]
[5630,11.149426999999999,5630,990.12991899999997,79.210635999999994,12.499961734936708]
[5640,11.266126999999999,5640,990.09216600000002,78.458189000000004,12.619360434128806]
[5650,11.383181,5650,990.05433200000004,77.717288999999994,12.73917740491437]
[5660,11.500595000000001,5660,990.016436,76.987683000000004,12.859413316802897]
[5670,11.618373,5670,989.97849499999995,76.269121999999996,12.980069378535655]
[5680,11.736522000000001,5680,989.940789,75.561368999999999,13.101149464351288]
[5690,11.855047000000001,5690,989.90177800000004,74.864197000000004,13.222632682482388]
[5700,11.973955,5700,989.863742,74.177355000000006,13.344554305016672]
[5710,12.093254999999999,5710,989.82566499999996,73.500631999999996,13.466900053321991]
[5720,12.212954,5720,989.78751799999998,72.83381,13.589671033274245]
[5730,12.333061000000001,5730,989.74928599999998,72.176678999999993,13.712868196665021]
[5740,12.453585,5740,989.71096999999997,71.529031000000003,13.836493465149834]
[5750,12.574536,5750,989.67258000000004,70.890666999999993,13.960548290510514]
[5760,12.695923000000001,5760,989.63413600000001,70.261390000000006,14.085034981516875]
[5770,12.817757,5770,989.59565799999996,69.641008999999997,{"$f":"D582/E582","v":14.209955774764838}]
[5780,12.940048000000001,5780,989.55715899999996,69.029338999999993,14.335312684944007]
[5790,13.062804,5790,989.51863900000001,68.426197999999999,14.461107995507803]
[5800,13.186033999999999,5800,989.48008600000003,67.831408999999994,14.587343836540386]
[5810,13.309747,5810,989.44147799999996,67.244802000000007,14.714021732118415]
[5820,13.433949,5820,989.40278599999999,66.666206000000003,14.841144342307405]
[5830,13.558643999999999,5830,989.36396200000001,66.095460000000003,14.968712858644148]
[5840,13.683837,5840,989.305566,65.532269999999997,15.096464169484745]
[5850,13.809528,5850,989.26772400000004,64.976737,15.224952339481129]
[5860,13.935717,5860,989.22879699999999,64.428601,15.353876720061017]
[5870,14.0624,5870,989.189798,63.887698999999998,15.483259116907623]
[5880,14.189572,5880,989.15074800000002,63.353887999999998,15.613102513929375]
[5890,14.317226,5890,989.11165800000003,62.827025999999996,15.74341045523944]
[5900,14.445351,5900,989.07252800000003,62.306977000000003,15.874185775374722]
[5910,14.573938,5910,989.03335000000004,61.793607999999999,16.005431338464653]
[5920,14.702973,5920,988.99410799999998,61.286785999999999,16.137150804416468]
[5930,14.832445,5930,988.95479399999999,60.786386,16.269346790908081]
[5940,14.962339999999999,5940,988.91540099999997,60.292282999999998,16.402022809453076]
[5950,15.092644999999999,5950,988.87593500000003,59.804355000000001,16.535182680257986]
[5960,15.22335,5960,988.83640500000001,59.322484000000003,16.668830067871063]
[5970,15.354442000000001,5970,988.79682700000001,58.846553999999998,16.802969074450818]
[5980,15.485913,5980,988.75721099999998,58.376452,16.937603727612633]
[5990,15.617756,5990,988.71756500000004,57.912067,17.072738312034346]
[6000,15.749965,6000,988.67887299999995,57.453301000000003,17.2083910896608]
[6010,15.882535000000001,6010,988.63367000000005,57.000050999999999,17.344434832172343]
[6020,16.015464999999999,6020,988.59380899999996,56.552185000000001,17.481089528194179]
[6030,16.148755000000001,6030,988.55390599999998,56.109620999999997,17.618260262353225]
[6040,16.282406000000002,6040,988.51393700000006,55.672260999999999,17.755950975298095]
[6050,16.416421,6050,988.47390399999995,55.240009999999998,17.894165913438467]
[6060,16.550802999999998,6060,988.43381399999998,54.812773999999997,18.032909883378647]
[6070,16.685559000000001,6070,988.39367600000003,54.390461999999999,18.172187542734974]
[6080,16.820694,6080,988.35350000000005,53.972985000000001,18.312003681100833]
[6090,16.956215,6090,988.31328699999995,53.560256000000003,18.452363017084906]
[6100,17.092129,6100,988.27302999999995,53.152189,18.593270542441818]
[6110,17.228445000000001,6110,988.23271799999998,52.748700999999997,18.734730889391951]
[6120,17.365169999999999,6120,988.19233499999996,52.349711999999997,18.876748261766942]
[6130,17.502313000000001,6130,988.15186900000003,51.955140999999998,19.019328019916259]
[6140,17.639882,6140,988.111313,51.564911000000002,19.162474904688576]
[6150,17.777885999999999,6150,988.07065899999998,51.178946000000003,19.306193976718472]
[6160,17.916333000000002,6160,988.02680399999997,50.797145,19.450439665457576]
[6170,18.055232,6170,987.98689000000002,50.419488000000001,19.595337620247154]
[6180,18.194590999999999,6180,987.94612900000004,50.045881000000001,19.740808019744922]
[6190,18.334419,6190,987.90534200000002,49.676251000000001,19.886873951095868]
[6200,18.474723000000001,6200,987.86451999999997,49.310530999999997,20.03354050273764]
[6210,18.615511999999999,6210,987.82365200000004,48.948653999999998,20.180813388658247]
[6220,18.756793999999999,6220,987.78271900000004,48.590555999999999,20.32869759712155]
[6230,18.898575999999998,6230,987.74170800000002,48.236173000000001,20.477198885574939]
[6240,19.040866999999999,6240,987.70061099999998,47.885443000000002,20.626322930749538]
[6250,19.183672999999999,6250,987.65942900000005,47.538305000000001,20.776075819278791]
[6260,19.327003000000001,6260,987.61817900000005,47.194699,20.926464198871148]
[6270,19.470863000000001,6270,987.57688099999996,46.854565999999998,21.077495008704169]
[6280,19.615262000000001,6280,987.53556000000003,46.517850000000003,21.229174607166925]
[6290,19.760206,6290,987.49423899999999,46.184493000000003,21.38151086772783]
[6300,19.905702999999999,6300,987.45293000000004,45.854441000000001,21.534510256051316]
[6310,20.051760000000002,6310,987.41164500000002,45.527642,21.688178908980177]
[6320,20.198383,6320,987.37025300000005,45.204045000000001,21.84251991165835]
[6330,20.345580999999999,6330,987.27558699999997,44.882748999999997,21.996771788644232]
[6340,20.493359999999999,6340,987.23394599999995,44.565387999999999,22.152481786986797]
[6350,20.641726999999999,6350,987.19227000000001,44.251075999999998,22.308887359032809]
[6360,20.790689,6360,987.15051700000004,43.939763999999997,22.465994969840988]
[6370,20.940253999999999,6370,987.10867299999995,43.631404000000003,22.62381180766037]
[6380,21.090427999999999,6380,987.06673799999999,43.325949999999999,22.782344945696519]
[6390,21.241219000000001,6390,987.024719,43.023356,22.941602207879832]
[6400,21.392634000000001,6400,986.98262399999999,42.723576999999999,23.101591517021152]
[6410,21.544678999999999,6410,986.94046500000002,42.426568000000003,{"$f":"D646/E646","v":23.262321500999089}]
[6420,21.697361999999998,6420,986.89824899999996,42.132286999999998,23.423799638505262]
[6430,21.850691000000001,6430,986.85598200000004,41.840691,23.586034513626938]
[6440,22.004673,6440,986.81366600000001,41.551741,23.749032946657998]
[6450,22.159313999999998,6450,986.771299,41.265394000000001,23.912804491821888]
[6460,22.314623000000001,6460,986.72887900000001,40.981611999999998,24.077356425120612]
[6470,22.470607000000001,6470,986.68639800000005,40.700355000000002,24.242697588264278]
[6480,22.627272999999999,6480,986.64379199999996,40.421582999999998,24.408836041873965]
[6490,22.78463,6490,986.60092599999996,40.145269999999996,24.5757700969504]
[6500,22.942682999999999,6500,986.55825700000003,39.871364999999997,24.743528519778547]
[6510,23.101443,6510,986.51553999999999,39.599836000000003,24.912111757230509]
[6520,23.260915000000001,6520,986.47276999999997,39.330649000000001,25.081527894441813]
[6530,23.421109000000001,6530,986.42994799999997,39.063769000000001,25.251786329168596]
[6540,23.582032000000002,6540,986.38707699999998,38.799160999999998,25.422897082748776]
[6550,23.743691999999999,6550,986.34415899999999,38.536793000000003,25.594868753090065]
[6560,23.906098,6560,986.30119300000001,38.276631000000002,25.767711714231066]
[6570,24.069257,6570,986.25817400000005,38.018644000000002,25.941434786574714]
[6580,24.233177999999999,6580,986.21509600000002,37.762799999999999,26.116047962545153]
[6590,24.397870000000001,6590,986.17195000000004,37.509067000000002,26.291561717597506]
[6600,24.563341000000001,6600,986.12873100000002,37.257415000000002,26.467985795579214]
[6610,24.729600000000001,6610,986.08544099999995,37.007815000000001,26.645329939095294]
[6620,24.896654999999999,6620,986.04209500000002,36.760235000000002,26.823606949193877]
[6630,25.064516000000001,6630,985.998741,36.514648000000001,27.002827495420465]
[6640,25.233191000000001,6640,985.94046100000003,36.270924000000001,27.182667334308881]
[6650,25.40269,6650,985.90583800000002,36.029133999999999,27.364128097000613]
[6660,25.573022000000002,6660,985.862211,35.789355999999998,27.546240591755829]
[6670,25.744195999999999,6670,985.81861400000003,35.551461000000003,27.729341812422277]
[6680,25.916221,6680,985.77501900000004,35.315421999999998,27.913442999491838]
[6690,26.089108,6690,985.731402,35.081212000000001,28.098556059009592]
[6700,26.262865999999999,6700,985.68773999999996,34.848806000000003,28.284691877248243]
[6710,26.437505000000002,6710,985.64401099999998,34.618178,28.471862701728554]
[6720,26.613033999999999,6720,985.60019899999998,34.389305,28.660079027476709]
[6730,26.789465,6730,985.55629799999997,34.162162000000002,28.84935379675326]
[6740,26.966805999999998,6740,985.51231700000005,33.936723999999998,29.039700974083416]
[6750,27.14507,6750,985.46826799999997,33.712969999999999,29.231131757302901]
[6760,27.324265,6760,985.42417,33.490875000000003,29.423661519742314]
[6770,27.504404000000001,6770,985.38003900000001,33.270417999999999,29.617302644048536]
[6780,27.685496000000001,6780,985.33588299999997,33.051575999999997,29.812069566667564]
[6790,27.867553999999998,6790,985.29170099999999,32.834327999999999,30.00797522032429]
[6800,28.050587,6800,985.24811899999997,32.618656000000001,30.205049496827826]
[6810,28.234608000000001,6810,985.20266500000002,32.404533999999998,30.40323508432493]
[6820,28.419627999999999,6820,985.15827300000001,32.191938,30.602639486942351]
[6830,28.605657999999998,6830,985.11380799999995,31.980851999999999,30.803238387770282]
[6840,28.792711000000001,6840,985.06926699999997,31.771256000000001,31.00504641679888]
[6850,28.980799000000001,6850,985.02466200000003,31.563130999999998,31.208078248003979]
[6860,29.169934000000001,6860,984.98000999999999,31.356456000000001,31.412351255511783]
[6870,29.360128,6870,984.93532600000003,31.151214,31.61787935455742]
[6880,29.551393999999998,6880,984.89062000000001,30.947386000000002,31.824678827478351]
[6890,29.743746000000002,6890,984.84588799999995,30.744952999999999,32.032766093348719]
[6900,29.937196,6900,984.80111499999998,30.543897999999999,32.242155699969928]
[6910,30.131758000000001,6910,984.75627799999995,30.344201999999999,32.452864570305721]
[6920,30.327445000000001,6920,984.71135000000004,30.145848000000001,32.664907950176094]
[6930,30.524272,6930,984.66630399999997,29.948817999999999,32.878302709642831]
[6940,30.722252999999998,6940,984.62111700000003,29.753095999999999,33.093064231029942]
[6950,30.921402,6950,984.57572200000004,29.558662999999999,33.309210298178918]
[6960,31.121735000000001,6960,984.44687799999997,29.364773,33.524756959640044]
[6970,31.323267000000001,6970,984.40429900000004,29.172877,33.743819610249616]
[6980,31.526012999999999,6980,984.35913000000005,28.982233000000001,33.964226634987028]
[6990,31.729990000000001,6990,984.31391199999996,28.792816999999999,34.186092732781233]
[7000,31.935213999999998,7000,984.26865599999996,28.604614000000002,34.409436743317002]
[7010,32.141703999999997,7010,984.22336099999995,28.417607,34.634280113733709]
[7020,32.349474999999998,7020,984.17801999999995,28.231783,34.860639868193942]
[7030,32.558548000000002,7030,984.13262399999996,28.047128000000001,35.088534697741601]
[7040,32.768940999999998,7040,984.08716600000002,27.863626,35.317986467375064]
[7050,32.980673000000003,7050,984.04164500000002,27.681263000000001,{"$f":"D710/E710","v":35.549015411616153}]
[7060,33.193765999999997,7060,983.99606500000004,27.500025999999998,35.781641260993723]
[7070,33.408240999999997,7070,983.95043299999998,27.319901000000002,36.015885745706029]
[7080,33.624121000000002,7080,983.90475700000002,27.140874,36.251771295205899]
[7090,33.841428000000001,7090,983.85903900000005,26.962933,36.489318094585634]
[7100,34.060186999999999,7100,983.81328099999996,26.786062999999999,36.728551000570711]
[7110,34.280425000000001,7110,983.76748099999998,26.610253,36.969489955619736]
[7120,34.502167999999998,7120,983.72156600000005,26.435490999999999,37.21215414534953]
[7130,34.725444000000003,7130,983.67562399999997,26.261741000000001,37.456603657769676]
[7140,34.950282999999999,7140,983.62962000000005,26.089033000000001,37.702801019876823]
[7150,35.176715000000002,7150,983.58354899999995,25.917335999999999,37.950796679103128]
[7160,35.404770999999997,7160,983.53742099999999,25.746637,38.200617074765923]
[7170,35.634483000000003,7170,983.49124300000005,25.576924999999999,38.45228630885066]
[7180,35.865884999999999,7180,983.445021,25.408189,38.705829093132138]
[7190,36.099007999999998,7190,983.39875400000005,25.240417000000001,38.961272074070727]
[7200,36.333886999999997,7200,983.35243500000001,25.073598,39.218640858802949]
[7210,36.570551000000002,7210,983.30605500000001,24.907720999999999,39.477961673008949]
[7220,36.809030999999997,7220,983.25960399999997,24.742775000000002,39.739261420758176]
[7230,37.049354999999998,7230,983.213076,24.578748999999998,40.002567909375699]
[7240,37.291545999999997,7240,983.166472,24.415633,40.267908351997264]
[7250,37.535625000000003,7250,983.11980000000005,24.253416000000001,40.535312633898663]
[7260,37.781609000000003,7260,983.07307200000002,24.092089999999999,40.804806556840859]
[7270,38.029508,7270,983.026298,23.931642,41.076425010870544]
[7280,38.279328999999997,7280,982.97964300000001,23.772057,41.350213950774219]
[7290,38.531073999999997,7290,982.93287499999997,23.613344000000001,41.626161673670609]
[7300,38.784742999999999,7300,982.88597300000004,23.455476999999998,41.904326780478613]
[7310,39.040329,7310,982.83902999999998,23.298449999999999,42.184738898939628]
[7320,39.297829,7320,982.79202599999996,23.142254000000001,42.467428885708365]
[7330,39.557236000000003,7330,982.74495100000001,22.986879999999999,42.752428820266168]
[7340,39.818545999999998,7340,982.69780200000002,22.832318999999998,43.039771912787316]
[7350,40.081755999999999,7350,982.65058699999997,22.678560999999998,43.329494627106193]
[7360,40.346870000000003,7360,982.60331699999995,22.525597999999999,43.62163068878349]
[7370,40.613894000000002,7370,982.55600600000002,22.373422000000001,43.916214783773356]
[7380,40.882840999999999,7380,982.50866399999995,22.222023,44.213286252111246]
[7390,41.153725999999999,7390,982.46129199999996,22.071393,44.512881085484722]
[7400,41.426574000000002,7400,982.41388500000005,21.921524000000002,44.815035898051612]
[7410,41.701408999999998,7410,982.36642800000004,21.772407000000001,45.119789833067145]
[7420,41.978262999999998,7420,982.31890699999997,21.624034000000002,45.427181024595129]
[7430,42.257171999999997,7430,982.27131099999997,21.476399000000001,45.737244451455759]
[7440,42.538170999999998,7440,982.22155499999997,21.329478000000002,46.049957481378584]
[7450,42.821300999999998,7450,982.207043,21.182997,46.367709111227271]
[7460,43.106603,7460,982.15944300000001,21.037517999999999,46.686089252543958]
[7470,43.394120000000001,7470,982.111718,20.892745999999999,47.0073066508347]
[7480,43.683895,7480,982.06391799999994,20.748673,47.331408519474955]
[7490,43.975974000000001,7490,982.01605400000005,20.60529,47.658443729741251]
[7500,44.270398999999998,7500,981.96812699999998,20.462592000000001,47.988452635912395]
[7510,44.567217999999997,7510,981.92013299999996,20.320568999999999,48.321488094157203]
[7520,44.866472999999999,7520,981.87206700000002,20.179216,48.65759239605741]
[7530,45.168210999999999,7530,981.82392800000002,20.038525,48.996816282635578]
[7540,45.472476999999998,7540,981.77572299999997,19.898489000000001,49.33920977617948]
[7550,45.779316000000001,7550,981.72746199999995,19.759101999999999,49.684821810221941]
[7560,46.088774000000001,7560,981.67915800000003,19.620356000000001,50.033707747198875]
[7570,46.400897000000001,7570,981.63082099999997,19.482247000000001,50.385913955407709]
[7580,46.715729000000003,7580,981.58245799999997,19.344764999999999,50.741503347288017]
[7590,47.033318000000001,7590,981.53406800000005,19.207906000000001,51.100524336176989]
[7600,47.35371,7600,981.48695999999995,19.071672,51.463078853285644]
[7610,47.676952,7610,981.43778499999996,18.936039999999998,51.82909335848467]
[7620,48.00309,7620,981.38917100000003,18.801006000000001,52.198758460052616]
[7630,48.332174000000002,7630,981.34048199999995,18.666568000000002,52.572089416758338]
[7640,48.664251999999998,7640,981.29172200000005,18.532719,52.949150202946477]
[7650,48.999372000000001,7650,981.24290599999995,18.399453000000001,53.330004212625227]
[7660,49.337586000000002,7660,981.19404799999995,18.266764999999999,53.714713470064346]
[7670,49.678941999999999,7670,981.14516100000003,18.134647000000001,54.103350398824965]
[7680,50.023493000000002,7680,981.09624499999995,18.003094999999998,54.495976664012495]
[7690,50.371290999999999,7690,981.04728899999998,17.872102000000002,{"$f":"D774/E774","v":54.8926639407049}]
[7700,50.722389,7700,980.99827700000003,17.741662000000002,55.293482482080876]
[7710,51.076841000000002,7710,980.94918800000005,17.611768999999999,55.698504108247171]
[7720,51.434702000000001,7720,980.90001400000006,17.482417000000002,56.107803286010167]
[7730,51.796028999999997,7730,980.85076100000003,17.3536,56.521457276876269]
[7740,52.160877999999997,7740,980.80145800000003,17.225313,56.939543449805527]
[7750,52.529308,7750,980.75215900000001,17.097549999999998,57.362145979979594]
[7760,52.901378999999999,7760,980.697137,16.970251999999999,57.78919116816887]
[7770,53.277151000000003,7770,980.67354,16.843463,58.2227977702685]
[7780,53.656685000000003,7780,980.62409500000001,16.717241999999999,58.659442448700574]
[7790,54.040045999999997,7790,980.57471699999996,16.591525000000001,59.100939606214617]
[7800,54.427297000000003,7800,980.52531799999997,16.466307,59.547372583299946]
[7810,54.818503999999997,7810,980.47583899999995,16.341581999999999,59.998832365189614]
[7820,55.213735,7820,980.42623400000002,16.217345999999999,60.455405835208801]
[7830,55.613059,7830,980.376485,16.093594,60.917187608933098]
[7840,56.016545000000001,7840,980.32660599999997,15.970319999999999,61.384280715727677]
[7850,56.424264999999998,7850,980.27663800000005,15.847522,61.856777229903834]
[7860,56.836292,7860,980.22663699999998,15.725193000000001,62.334792138958164]
[7870,57.252701999999999,7870,980.17665399999998,15.603332,62.818419424774142]
[7880,57.673571000000003,7880,980.12671399999999,15.481932,63.307777995666171]
[7890,58.098976999999998,7890,980.07680900000003,15.360991,63.802967464794428]
[7900,58.529000000000003,7900,980.02689699999996,15.240505000000001,64.304096025689432]
[7910,58.963721999999997,7910,979.97691899999995,15.120467,64.811286516481275]
[7920,59.403225999999997,7920,979.92713000000003,15.000878999999999,65.324647309001037]
[7930,59.847599000000002,7930,979.87686599999995,14.88172,65.844328881338981]
[7940,60.296928000000001,7940,979.82639700000004,14.763005,66.37038983594465]
[7950,60.751302000000003,7950,979.77580699999999,14.644724999999999,66.902984316878602]
[7960,61.210813000000002,7960,979.72518700000001,14.526876,67.442248904719776]
[7970,61.675555000000003,7970,979.67462799999998,14.409454999999999,67.988319336158099]
[7980,62.145625000000003,7980,979.624188,14.29246,68.541327944944399]
[7990,62.621119,7990,979.57386599999995,14.175888,69.101411213181137]
[8000,63.102139999999999,8000,979.52359200000001,14.059735,69.668709403128872]
[8010,63.588788999999998,8010,979.47323200000005,13.943997,70.243362215295946]
[8020,64.081173000000007,8020,979.42262300000004,13.828671,70.825506153122021]
[8030,64.579400000000007,8030,979.37162000000001,13.713751,71.415298411062011]
[8040,65.083579999999998,8040,979.32014200000003,13.599235999999999,72.012879399989828]
[8050,65.593826000000007,8050,979.26822000000004,13.485120999999999,72.618422927017122]
[8060,66.110254999999995,8060,979.21603100000004,13.371407,73.232086271848587]
[8070,66.632986000000002,8070,979.16406900000004,13.258092,73.85407108353148]
[8080,67.162139999999994,8080,982.79279199999996,13.158712,74.687613194969231]
[8090,67.697843000000006,8090,982.73118099999999,13.045665,75.330094786275751]
[8100,68.240223,8100,982.67043799999999,12.932999000000001,75.981637205724667]
[8110,68.789410000000004,8110,982.61035200000003,12.820732,76.642297179287425]
[8120,69.34554,8120,982.55079999999998,12.708864,77.312244430344052]
[8130,69.908749999999998,8130,982.49161600000002,12.597391,77.99167430779913]
[8140,70.479181999999994,8140,982.43260099999998,12.486311000000001,78.680772968092811]
[8150,71.056980999999993,8150,982.373559,12.375622,79.379732105586285]
[8160,71.642296000000002,8160,982.31434300000001,12.265321,80.088759438093788]
[8170,72.235279000000006,8170,982.25488099999995,12.155407,80.808061877319275]
[8180,72.836087000000006,8180,982.19518200000005,12.045878999999999,81.537858881033102]
[8190,73.444880999999995,8190,982.13531399999999,11.936738,82.278367339552901]
[8200,74.061824999999999,8200,982.075379,11.827984000000001,83.029819705538998]
[8210,74.687089,8210,982.01546900000005,11.719617,83.792454053745956]
[8220,75.320846000000003,8220,981.95564000000002,11.611639,84.566497460005436]
[8230,75.963273999999998,8230,981.89589899999999,11.504049,85.352200690383015]
[8240,76.614557000000005,8240,981.83547799999997,11.396843000000001,86.149776565317254]
[8250,77.274883000000003,8250,981.778323,11.290013,86.959893048838822]
[8260,77.944444000000004,8260,981.71854699999994,11.183589,87.782065936078297]
[8270,78.623437999999993,8270,981.65861399999994,11.077553999999999,88.616910736792619]
[8280,79.312067999999996,8280,981.59853099999998,10.971909999999999,89.464690377518593]
[8290,80.010544999999993,8290,981.53832899999998,10.866656000000001,90.325701761425037]
[8300,80.719082,8300,981.47805900000003,10.761794999999999,91.200218829665502]
[8310,81.437899999999999,8310,981.41777500000001,10.657329000000001,92.088531282087658]
[8320,82.167225999999999,8320,981.35751500000003,10.553258,92.990952651778258]
[8330,82.907292999999996,8330,981.29728599999999,10.449585000000001,{"$f":"D838/E838","v":93.90777585904128}]
[8340,83.658338999999998,8340,981.23706900000002,10.346313,94.839298695100368]
[8350,84.420612000000006,8350,981.17682400000001,10.243441000000001,95.785861801712912]
[8360,85.194363999999993,8360,981.11650999999995,10.140973000000001,96.747768680579256]
[8370,85.979854000000003,8370,981.05610000000001,10.038911000000001,97.725350887162961]
[8380,86.777350999999996,8380,980.99559499999998,9.9372579999999999,98.718941885175965]
[8390,87.587129000000004,8390,980.93503399999997,9.8360160000000008,99.728897756978014]
[8400,88.409470999999996,8400,980.88198299999999,9.7352480000000003,100.75572630507205]
[8410,89.244668000000004,8410,980.82012199999997,9.6348470000000006,101.79924206372969]
[8420,90.093018000000001,8420,980.75942199999997,9.5348600000000001,102.86039039902002]
[8430,90.954830000000001,8430,980.69874200000004,9.4353020000000001,103.93930602327302]
[8440,91.830420000000004,8440,980.63806399999999,9.3361750000000008,105.03638417231895]
[8450,92.720112,8450,980.57735300000002,9.2374829999999992,106.15200623373273]
[8460,93.624243000000007,8460,980.51657499999999,9.1392330000000008,107.2865277644196]
[8470,94.543158000000005,8470,980.45570299999997,9.0414270000000005,108.44037152542401]
[8480,95.477209000000002,8480,980.39473299999997,8.9440720000000002,109.61391332717356]
[8490,96.426764000000006,8490,980.33367799999996,8.8471729999999997,110.80756282261011]
[8500,97.392195999999998,8500,980.27256899999998,8.7507339999999996,112.02175371803096]
[8510,98.373892999999995,8510,980.21143700000005,8.6547619999999998,113.25689106182239]
[8520,99.372253000000001,8520,980.15030300000001,8.5592629999999996,114.51339945974321]
[8530,100.387685,8530,980.08917099999996,8.4642400000000002,115.79175106093399]
[8540,101.42061099999999,8540,980.02802299999996,8.3696999999999999,117.09237165011888]
[8550,102.471463,8550,979.96682399999997,8.2756469999999993,118.41573522891927]
[8560,103.54069,8560,979.90474600000005,8.1820789999999999,119.76231786566716]
[8570,104.62875,8570,979.85410400000001,8.0890419999999992,121.13351667601678]
[8580,105.736116,8580,979.79274199999998,7.9964750000000002,122.52808168599289]
[8590,106.863275,8590,979.73126300000001,7.9044100000000004,123.94742466547154]
[8600,108.010728,8600,979.669714,7.8128500000000001,125.39210582565902]
[8610,109.17899,8610,979.60813399999995,7.7218,126.86266595871429]
[8620,110.36859200000001,8620,979.54655100000002,7.6312600000000002,128.35974020017665]
[8630,111.580077,8630,979.48497599999996,7.5412350000000004,129.88389514449554]
[8640,112.814008,8640,979.42340200000001,7.4517249999999997,131.43579533597926]
[8650,114.070961,8650,979.361805,7.3627349999999998,133.01603344409381]
[8660,115.351529,8660,979.30015600000002,7.2742639999999996,134.62532511880241]
[8670,116.65631999999999,8670,979.23842999999999,7.1863169999999998,136.26429644002624]
[8680,117.985961,8680,979.17661799999996,7.0988949999999997,137.93366685941967]
[8690,119.341095,8690,979.11472500000002,7.0120009999999997,139.63413938474909]
[8700,120.722379,8700,979.05277599999999,6.9256399999999996,141.3663973293443]
[8710,122.130492,8710,978.99080800000002,6.8398149999999998,143.13118234923022]
[8720,123.56612699999999,8720,978.93001400000003,6.7545409999999997,144.92916898424335]
[8730,125.029994,8730,978.86770999999999,6.6698009999999996,146.76115674215768]
[8740,126.52282099999999,8740,978.80571799999996,6.5856199999999996,148.62772495224445]
[8750,128.045354,8750,978.743694,6.5020009999999999,150.52961296068702]
[8760,129.59835200000001,8760,978.68161299999997,6.4189540000000003,152.46746011889164]
[8770,131.18259399999999,8770,978.61945200000002,6.3364900000000004,154.44188375583326]
[8780,132.79887199999999,8780,978.55719499999998,6.2546210000000002,156.45347575816345]
[8790,134.44799599999999,8790,978.49484500000005,6.1733589999999996,158.5028256092024]
[8800,136.130788,8800,978.43242199999997,6.0927210000000001,160.59038679105771]
[8810,137.848085,8810,978.369956,6.0127230000000003,162.71661874328819]
[8820,139.600739,8820,978.30747899999994,5.9333830000000001,164.88190278631936]
[8830,141.38960900000001,8830,978.24501299999997,5.8547209999999996,167.0865294862044]
[8840,143.21557000000001,8840,978.18256699999995,5.7767590000000002,169.33068646277263]
[8850,145.07950299999999,8850,978.12013000000002,5.6995189999999996,171.61450466258646]
[8860,146.98229799999999,8860,978.05767500000002,5.6230270000000004,173.93792969516241]
[8870,148.92484899999999,8870,977.99515299999996,5.5473090000000003,176.30082495855197]
[8880,150.90805499999999,8880,977.935607,5.4724259999999996,178.70239031098822]
[8890,152.93281500000001,8890,977.84284600000001,5.3992719999999998,181.10642434757872]
[8900,155.00002699999999,8900,977.78018399999996,5.3260630000000004,183.58404397394472]
[8910,157.11058,8910,977.71740199999999,5.2537529999999997,186.09885200160724]
[8920,159.26535699999999,8920,977.65453200000002,5.1823759999999996,188.64986484963654]
[8930,161.46522300000001,8930,977.59159299999999,5.1119690000000002,191.2358218525973]
[8940,163.711026,8940,977.528595,5.0425700000000004,193.85523552474231]
[8950,166.00358499999999,8950,977.46554400000002,4.9742199999999999,196.50629525835208]
[8960,168.34368699999999,8960,977.40244199999995,4.9069609999999999,199.18691874665399]
[8970,170.732079,8970,977.33928600000002,4.8408360000000004,{"$f":"D902/E902","v":201.89473181904941}]
[8980,173.169456,8980,977.27607799999998,4.7758919999999998,204.62692163055613]
[8990,175.656454,8990,977.21282099999996,4.7121750000000002,207.38041795985927]
[9000,178.19363799999999,9000,977.14952300000004,4.6497349999999997,210.15165875044494]
[9010,180.781488,9010,977.08619299999998,4.588622,212.93673634481115]
[9020,183.42038700000001,9020,977.02283699999998,4.5288899999999996,215.73119174897161]
[9030,186.110604,9030,976.95945700000004,4.4705909999999998,218.53026971154375]
[9040,188.85227800000001,9040,976.89554799999996,4.4137750000000002,221.32880538767833]
[9050,191.6454,9050,976.83288900000002,4.3585070000000004,224.12098661307644]
[9060,194.489788,9060,976.76940300000001,4.304843,226.90012225765261]
[9070,197.38507100000001,9070,976.70583499999998,4.2528389999999998,229.65972495079171]
[9080,200.330659,9080,976.64218900000003,4.202553,232.39259302619146]
[9090,203.32571999999999,9090,976.57847300000003,4.1540439999999998,235.0910276829037]
[9100,206.36914899999999,9100,976.51470200000006,4.1073729999999999,237.74677926742959]
[9110,209.45953900000001,9110,976.45089599999994,4.0625989999999996,240.35128645480395]
[9120,212.595146,9120,976.38707499999998,4.019781,242.89558933683202]
[9130,215.77385799999999,9130,976.32324900000003,3.9789759999999998,245.37047949020052]
[9140,218.993154,9140,976.25941899999998,3.940242,247.76636028954567]
[9150,222.250069,9150,976.19556799999998,3.9036330000000001,250.0736027182883]
[9160,225.54115300000001,9160,976.13167099999998,3.869202,252.28242697072935]
[9170,228.862435,9170,976.06768699999998,3.8369979999999999,254.38316282677238]
[9180,232.20937599999999,9180,976.00356599999998,3.80707,256.36606786846579]
[9190,235.57683599999999,9190,975.93918599999995,3.7794599999999998,258.2218586782239]
[9200,238.95903300000001,9200,976.02201600000001,3.7549619999999999,259.92860007637893]
[9210,242.34950599999999,9210,975.95284900000001,3.7320820000000001,261.50359209685104]
[9220,245.74108799999999,9220,975.88840400000004,3.7116259999999999,262.92746198027498]
[9230,249.12587500000001,9230,975.82381699999996,3.6936209999999998,264.19164743756875]
[9240,252.49520999999999,9240,975.75915299999997,3.678086,265.28992334600116]
[9250,255.83967100000001,9250,975.69444099999998,3.6650369999999999,266.21680517822875]
[9260,259.149069,9260,975.62969899999996,3.6544810000000001,266.96805893914893]
[9270,262.412462,9270,975.564933,3.64642,267.54047339582382]
[9280,265.61818199999999,9280,975.50014199999998,3.6408499999999999,267.93197797217681]
[9290,268.75387999999998,9290,975.43532000000005,3.6377609999999998,268.14167285866228]
[9300,271.80658199999999,9300,975.37045899999998,3.6371380000000002,268.16976947259081]
[9310,274.76277499999998,9310,975.30555400000003,3.6389580000000001,268.0178100434245]
[9320,277.60851000000002,9320,975.24059999999997,3.6431960000000001,267.68820563044096]
[9330,280.329519,9330,975.17559200000005,3.6498189999999999,267.1846444988094]
[9340,282.91136699999998,9340,975.11053000000004,3.6587930000000002,266.51153262838318]
[9350,285.339608,9350,975.04540799999995,3.670077,265.67437358943693]
[9360,287.59997600000003,9360,974.97978699999999,3.6836319999999998,264.67893291186527]
[9370,289.67857199999997,9370,974.91562199999998,3.6994250000000002,263.53166289355778]
[9380,291.56207899999998,9380,974.85038999999995,3.7173799999999999,262.24125324825548]
[9390,293.23797200000001,9390,974.78511000000003,3.737463,260.81465154303868]
[9400,294.69473099999999,9400,974.71978799999999,3.7596280000000002,259.25963632572154]
[9410,295.92205000000001,9410,974.65442499999995,3.7838250000000002,257.58443506240377]
[9420,296.91102799999999,9420,974.589021,3.8100079999999998,255.79710620030195]
[9430,297.65434399999998,9430,974.52357400000005,3.8381280000000002,253.90595988461041]
[9440,298.14640200000002,9440,974.45808399999999,3.8681410000000001,251.9189667594847]
[9450,298.38345099999998,9450,974.39254900000003,3.9000010000000001,249.84417927072326]
[9460,298.36365699999999,9460,974.32696999999996,3.9336679999999999,247.68917203993828]
[9470,298.08714600000002,9470,974.261349,3.9690989999999999,245.46158939346185]
[9480,297.55599799999999,9480,974.19569000000001,4.0062559999999996,243.16860679896644]
[9490,296.77420799999999,9490,974.13000099999999,4.045102,240.81716629148042]
[9500,295.74759299999999,9500,974.06428800000003,4.0856019999999997,238.4138954308325]
[9510,294.48368399999998,9510,973.99856899999997,4.1277200000000001,235.96527114242244]
[9520,292.99156499999998,9520,973.93940299999997,4.1713269999999998,233.48430918985733]
[9530,291.281701,9530,973.87251700000002,4.216577,230.96282055325921]
[9540,289.365745,9540,973.80663600000003,4.2633640000000002,228.41273604599562]
[9550,287.25632300000001,9550,973.74069299999996,4.3116440000000003,225.8397708623439]
[9560,284.96683000000002,9560,973.67468699999995,4.361389,223.24876020001884]
[9570,282.51121000000001,9570,973.60862099999997,4.4125690000000004,220.64439581568013]
[9580,279.90375599999999,9580,973.54249600000003,4.4651560000000003,218.03101526576003]
[9590,277.15891399999998,9590,973.47632099999998,4.5191210000000002,215.41275858734474]
[9600,274.29110400000002,9600,973.41010400000005,4.5744340000000001,212.79356178272548]
[9610,271.31455999999997,9610,973.34385199999997,4.6310669999999998,{"$f":"D966/E966","v":210.17701795288212}]
[9620,268.24319200000002,9620,973.27756799999997,4.6889909999999997,207.56652507970264]
[9630,265.090463,9630,973.21124899999995,4.7481749999999998,204.96532857360987]
[9640,261.86929500000002,9640,973.14488900000003,4.8085899999999997,202.37634920007739]
[9650,258.59198700000002,9650,973.07847800000002,4.8702069999999997,199.80228314730772]
[9660,255.270161,9660,973.01200800000004,4.932995,197.24569110651845]
[9670,251.914714,9670,972.94546800000001,4.9969270000000003,194.70876160488234]
[9680,248.53579999999999,9680,972.87973999999997,5.0619769999999997,192.19363106549082]
[9690,245.14281500000001,9690,972.80877099999998,5.128088,189.70204313966531]
[9700,241.74439599999999,9700,972.74204699999996,5.195271,187.23605505853303]
[9710,238.34842900000001,9710,972.67531199999996,5.2634819999999998,184.7969294850823]
[9720,234.962073,9720,972.60855700000002,5.3326929999999999,182.38600215688396]
[9730,231.59177500000001,9730,972.54178200000001,5.402876,180.00446095746042]
[9740,228.24330699999999,9740,972.47497999999996,5.4740039999999999,177.6533192156966]
[9750,224.92179400000001,9750,972.408141,5.5460520000000004,175.33339770344742]
[9760,221.63175100000001,9760,972.34125700000004,5.6189939999999998,173.04543428948315]
[9770,218.377118,9770,972.27431999999999,5.6928049999999999,170.7900270604737]
[9780,215.161305,9780,972.20732699999996,5.7674620000000001,168.56761726388487]
[9790,211.987225,9790,972.14028299999995,5.8429409999999997,166.37858965202628]
[9800,208.857338,9800,972.07319299999995,5.9192200000000001,164.22319038657119]
[9810,205.773685,9810,972.00606500000004,5.9962770000000001,162.10159487295201]
[9820,202.737933,9820,971.93890099999999,6.0740910000000001,160.01388536984382]
[9830,199.751406,9830,971.87169900000004,6.1526420000000002,157.96005992222527]
[9840,196.815121,9840,971.80304100000001,6.2319009999999997,155.94006403503522]
[9850,193.929822,9850,971.73624600000005,6.3118720000000001,153.95373131774537]
[9860,191.096011,9860,971.66894600000001,6.3925200000000002,152.00092389229911]
[9870,188.313973,9870,971.60157800000002,6.4738319999999998,150.08137035375648]
[9880,185.58380500000001,9880,971.53414599999996,6.5557889999999999,148.19484672249214]
[9890,182.905439,9890,971.46665800000005,6.6383760000000001,146.34101141604515]
[9900,180.27866299999999,9900,971.39912100000004,6.7215769999999999,144.51952584936541]
[9910,177.70314099999999,9910,971.331547,6.8053780000000001,142.72999192697304]
[9920,175.178426,9920,971.26394300000004,6.8897620000000002,140.97206013792641]
[9930,172.70398399999999,9930,971.19631300000003,6.9747170000000001,139.24526443151743]
[9940,170.27919900000001,9940,971.12865399999998,7.0602289999999996,137.54917213025243]
[9950,167.903389,9950,971.06095700000003,7.1462839999999996,135.88334258756021]
[9960,165.575819,9960,970.99321099999997,7.2328700000000001,134.24729201547933]
[9970,163.29570699999999,9970,970.92540499999996,7.3199759999999996,132.64051753721597]
[9980,161.06223299999999,9980,970.85753099999999,7.407591,131.06251830048393]
[9990,158.874549,9990,970.78957600000001,7.4957019999999996,129.51282961889362]
[10000,156.73178200000001,10000,970.72499800000003,7.5842780000000003,127.99174792907117]

{"sheet":"Overhead Line","index":1,"n_rows":2052,"n_cols":6,"rows_kept":2052,"cut":false,"hidden":false,"merged":[[0,0,0,1]]}
["Frequency Sweep Calculation",null,"EMT Time Domain Simulation",null,null,"EMT / FFT"]
[null,null,"FFT - Core_Send m U A(1)","FFT - Core_Send m U A(1)","FFT - Core m I bus1 A(2)"]
["Freq.Sweep","Core_Send","FFT - Core_Send m U A(1)","Core_Send","Overhead Line","hand calculation"]
["Frequency in Hz","Z, Magnitude A in Ohm","Frequency in Hz","FFT Mag, Phase Voltage A in V","FFT Mag, Phase Current A/Terminal i in A","Z (f)= U(f) / I(f)"]
[0,7272573944701.0898,0,1.136107,1.237E-3,{"$f":"D5/E5","v":918.4373484236055}]
[10,45679.223281999999,10,1002.272186,2.3064999999999999E-2,{"$f":"D6/E6","v":43454.246087145031}]
[20,22836.187054999999,20,1002.272098,4.9235000000000001E-2,20356.902569310449]
[30,15220.507564,30,1002.2719530000001,7.5132000000000004E-2,13340.147380610126]
[40,11411.685783999999,40,1002.27175,0.100911,9932.2348406021138]
[50,9125.6030300000002,50,1002.27149,0.126581,7918.0247430499048]
[60,7600.8853630000003,60,1002.27117,0.15215500000000001,6587.1720942459988]
[70,6511.2312449999999,70,1002.2707789999999,0.17763399999999999,5642.336371415382]
[80,5693.4910950000003,80,1002.271283,0.203039,4936.3485980525911]
[90,5057.0268980000001,90,1002.265492,0.22836200000000001,4388.9328872579499]
[100,4547.4561519999997,100,1002.264877,0.25371700000000003,3950.3260601378697]
[110,4130.1719400000002,110,1002.264229,0.27908100000000002,3591.3022706669385]
[120,3782.1030230000001,120,1002.26354,0.30446200000000001,3291.9166923951102]
[130,3487.277004,130,1002.2628120000001,0.32986900000000002,3038.3661756636725]
[140,3234.2850010000002,140,1002.262049,0.35531699999999999,2820.7545628269968]
[150,3014.7604660000002,150,1002.261248,0.38080999999999998,2631.9194558966415]
[160,2822.428449,160,1002.260402,0.40635300000000002,2466.4771811700662]
[170,2652.4904200000001,170,1002.259502,0.43195299999999998,2320.2975833018872]
[180,2501.214148,180,1002.258538,0.45761600000000002,2190.173722072655]
[190,2365.6530980000002,190,1002.257504,0.48334100000000002,2073.6033235334889]
[200,2243.450002,200,1002.2564,0.50911300000000004,1968.6325039824162]
[210,2132.6965639999999,210,1002.255229,0.53488999999999998,1873.7595187795623]
[220,2031.8314150000001,220,1002.254003,0.56060399999999999,1787.811009197223]
[230,1939.564697,230,1002.2527260000001,0.58616199999999996,1709.8561933390431]
[240,1854.821496,240,1002.250212,0.61146800000000001,1639.0885737274887]
[250,1776.698858,250,1002.24934,0.63648400000000005,1574.6654118563858]
[260,1704.432716,260,1002.247972,0.66139400000000004,1515.3569158474372]
[270,1637.372171,270,1002.246534,0.68680600000000003,1459.2862234750423]
[280,1574.959286,280,1002.245016,0.713565,1404.5602236656787]
[290,1516.7130569999999,290,1002.243408,0.74209899999999995,1350.5521608302936]
[300,1462.2165890000001,300,1002.241714,0.77214000000000005,1298.0051726370864]
[310,1411.1067599999999,310,1002.239947,0.80321799999999999,1247.780735740484]
[320,1363.065818,320,1002.238129,0.835032,1200.2391872407284]
[330,1317.8145039999999,330,1002.2362879999999,0.86726400000000003,1155.629990406612]
[340,1275.106397,340,1002.2344430000001,0.898702,1115.202194943374]
[350,1234.7232180000001,350,1002.232601,0.92576000000000003,1082.6052119339786]
[360,1196.470924,360,1002.230744,0.94506800000000002,1060.4853238073874]
[370,1160.176434,370,1002.228832,0.96248999999999996,1041.2875271431392]
[380,1125.6848680000001,380,1002.226798,0.98511099999999996,1017.3744867329672]
[390,1092.8572160000001,390,1002.224529,1.0122359999999999,990.10954856377373]
[400,1061.5683550000001,400,1002.22591,1.0415369999999999,962.25665530845288]
[410,1031.7053530000001,410,1001.647364,1.069088,936.91760079619269]
[420,1003.16602,420,1001.644433,1.0998129999999999,910.74067409641464]
[430,975.85765700000002,430,1001.6410530000001,1.1308450000000001,885.74566187231665]
[440,949.69597999999996,440,1001.637463,1.162134,861.89498199002867]
[450,924.60418200000004,450,1001.6337600000001,1.1936960000000001,839.10288716725199]
[460,900.51212399999997,460,1001.630008,1.2255510000000001,817.28953589038724]
[470,877.35562200000004,470,1001.626245,1.257706,796.39140228320457]
[480,855.07583,480,1001.622484,1.290178,776.34441449164376]
[490,833.61869100000001,490,1001.6187169999999,1.3229930000000001,757.08542448826256]
[500,812.93446300000005,500,1001.614923,1.356176,738.55821294581233]
[510,792.97729200000003,510,1001.611074,1.3897470000000001,720.71468691783468]
[520,773.70484099999999,520,1001.6071470000001,1.4237219999999999,703.51314863435425]
[530,755.07795499999997,530,1001.60313,1.4581109999999999,686.91830045860706]
[540,737.06037000000003,540,1001.599022,1.492928,670.89573107343415]
[550,719.61844699999995,550,1001.594825,1.5281940000000001,655.41078226979039]
[560,702.72093800000005,560,1001.589726,1.5639350000000001,640.42925441274735]
[570,686.33877800000005,570,1001.585928,1.600168,625.92548282430346]
[580,670.44489599999997,580,1001.581605,1.6369180000000001,611.87035941934778]
[590,655.01404400000001,590,1001.577244,1.674213,598.23764598650234]
[600,640.02264600000001,600,1001.572838,1.712075,585.00523516785188]
[610,625.44866400000001,610,1001.5683780000001,1.750521,572.1544488755062]
[620,611.27146900000002,620,1001.563858,1.7895719999999999,559.66670131182207]
[630,597.47172999999998,630,1001.559276,1.829256,547.52275023288155]
[640,584.03131699999994,640,1001.554632,1.8696010000000001,535.70501513424517]
[650,570.93320100000005,650,1001.549932,1.910631,{"$f":"D70/E70","v":524.19851452216574}]
[660,558.16137800000001,660,1001.545177,1.952366,512.99048282955141]
[670,545.70078699999999,670,1001.540365,1.9948239999999999,502.06953846554882]
[680,533.53724399999999,680,1001.535487,2.0380400000000001,491.42091764636609]
[690,521.65737300000001,690,1001.53053,2.0820850000000002,481.02288331168029]
[700,510.04855700000002,700,1001.525478,2.126989,470.86537730096393]
[710,498.69887599999998,710,1001.52031,2.1727539999999999,460.94510008956377]
[720,487.59706199999999,720,1001.527539,2.2192440000000002,451.29221437570629]
[730,476.73245500000002,730,1001.518718,2.266753,441.82966472306424]
[740,466.09495900000002,740,1001.513388,2.3151449999999998,432.59207868189685]
[750,455.67500899999999,750,1001.507989,2.3645130000000001,423.55782734119032]
[760,445.46352899999999,760,1001.502559,2.4153199999999999,414.64590985873508]
[770,435.45190700000001,770,1001.497117,2.4680749999999998,405.78066590358884]
[780,425.63196199999999,780,1001.491664,2.5223409999999999,397.04848154948121]
[790,415.99591400000003,790,1001.486191,2.5776349999999999,388.52909391748636]
[800,406.53636499999999,800,1001.480677,2.6339739999999998,380.21661451479781]
[810,397.24626999999998,810,1001.4751,2.6915089999999999,372.086847935489]
[820,388.11891800000001,820,1001.469441,2.7503600000000001,364.12303880219315]
[830,379.14791000000002,830,1001.463693,2.8106170000000001,356.31453627441948]
[840,370.32714299999998,840,1001.457857,2.8723770000000002,348.65125887026664]
[850,361.65078999999997,850,1001.451947,2.935775,341.12012909708682]
[860,353.11328500000002,860,1001.44598,3.0009730000000001,333.70709433240484]
[870,344.70930700000002,870,1001.439964,3.0680860000000001,326.40544104695891]
[880,336.43376999999998,880,1001.434196,3.1371739999999999,319.2153817416567]
[890,328.28180200000003,890,1001.427038,3.2082700000000002,312.13926446340241]
[900,320.24874199999999,900,1001.4209059999999,3.2814380000000001,305.17745756585981]
[910,312.33012200000002,910,1001.414731,3.3567309999999999,298.33034908069783]
[920,304.52166,920,1001.40849,3.434247,291.59477754512125]
[930,296.81924900000001,930,1001.4021729999999,3.5141450000000001,284.96324795931866]
[940,289.21894800000001,940,1001.3957789999999,3.596657,278.42404182550627]
[950,281.716973,950,1001.389319,3.6820560000000002,271.96471726665754]
[960,274.30969199999998,960,1001.382807,3.7706050000000002,265.57616271128899]
[970,266.99361199999998,970,1001.376258,3.8625319999999999,259.25384126267431]
[980,259.765379,980,1001.369681,3.95804,252.99635198229427]
[990,252.62176600000001,990,1001.363075,4.0573350000000001,246.80315404076813]
[1000,245.55967100000001,1000,1001.356431,4.1606519999999998,240.67295967074392]
[1010,238.57611199999999,1010,1001.34973,4.2682599999999997,234.60373313715661]
[1020,231.668217,1020,1001.342948,4.3804610000000004,228.5930517358789]
[1030,224.83322699999999,1030,1001.336048,4.4976079999999996,222.63746595968348]
[1040,218.068488,1040,1001.313369,4.6201369999999997,216.72806866982518]
[1050,211.37144799999999,1050,1001.307375,4.7483370000000003,210.87538121241184]
[1060,204.73965699999999,1060,1001.300371,4.8825120000000002,205.07893703077431]
[1070,198.170761,1070,1001.2932939999999,5.0227459999999997,199.35176773820535]
[1080,191.66250400000001,1080,1001.286165,5.169092,193.70639272816192]
[1090,185.212726,1090,1001.27899,5.3219019999999997,188.14307178147965]
[1100,178.819365,1100,1001.2717709999999,5.4820200000000003,182.64650092484155]
[1110,172.48045400000001,1110,1001.264501,5.6506179999999997,177.19557418321324]
[1120,166.194129,1120,1001.257171,5.8288060000000002,171.7774053554021]
[1130,159.958628,1130,1001.249773,6.0175989999999997,166.38692159447649]
[1140,153.772301,1140,1001.242303,6.2180330000000001,161.02235272794468]
[1150,147.633613,1150,1001.234763,6.4312449999999997,155.68288301876231]
[1160,141.54116099999999,1160,1001.227161,6.6585330000000003,150.36753005504366]
[1170,135.49368000000001,1170,1001.219508,6.90144,145.07400020865211]
[1180,129.49006900000001,1180,1001.211815,7.1617829999999998,139.79923923972564]
[1190,123.52941,1190,1001.204085,7.4416669999999998,134.54029654914686]
[1200,117.611002,1200,1001.197353,7.743544,129.29446168317762]
[1210,111.734404,1210,1001.183455,8.0702390000000008,124.05871189192784]
[1220,105.89949,1220,1001.175507,8.4250299999999996,118.83346492534746]
[1230,100.106526,1230,1001.167523,8.811439,113.62134187162846]
[1240,94.356269999999995,1240,1001.15948,9.2330830000000006,108.43176434133647]
[1250,88.650114000000002,1250,1001.151376,9.6930630000000004,103.28534705696228]
[1260,82.990279999999998,1260,1001.1432160000001,10.192829,98.220348443008319]
[1270,77.380097000000006,1270,1001.135006,10.730546,93.297676185349744]
[1280,71.824392000000003,1280,1001.126754,11.299837999999999,88.596558109948134]
[1290,66.330077000000003,1290,1001.11846,11.891394999999999,{"$f":"D134/E134","v":84.188479148157143}]
[1300,60.907010999999997,1300,1001.110121,12.500128,80.087989578986708]
[1310,55.569322999999997,1310,1001.101726,13.135247,76.214914420718543]
[1320,50.337470000000003,1320,1001.093264,13.823694,72.418650470706311]
[1330,45.241504999999997,1330,1001.0847240000001,14.602556,68.555444950870253]
[1340,40.326351000000003,1340,1001.076098,15.509354,64.546601876519162]
[1350,35.660322999999998,1350,1001.067377,16.579325999999998,60.38046281254136]
[1360,31.348514999999999,1360,1001.055683,17.849435,56.083326054858325]
[1370,27.551721000000001,1370,1001.047667,19.364967,51.693745050017384]
[1380,24.505092999999999,1380,1001.0388349999999,21.187225999999999,47.247281687560232]
[1390,22.510867000000001,1390,1001.029977,23.403020999999999,42.773536672893641]
[1400,21.855993999999999,1400,1001.021087,26.138736000000002,38.296461121914994]
[1410,22.655450999999999,1410,1001.012154,29.583463999999999,33.836881103578676]
[1420,24.768792000000001,1420,1001.003163,34.029325,29.415898287726836]
[1430,27.900169000000002,1430,1000.994097,39.943851000000002,25.060029815352554]
[1440,31.751818,1440,1000.984947,48.098229000000003,20.811264111200433]
[1450,36.096587999999997,1450,1000.9757070000001,59.750143000000001,16.75269140360049]
[1460,40.780358999999997,1460,1000.966368,76.465508999999997,13.090429673331542]
[1470,45.702601999999999,1470,1000.95687,95.841565000000003,10.443870256083569]
[1480,50.797922999999997,1480,1000.9472040000001,95.243067999999994,10.509396904350037]
[1490,56.023249999999997,1490,1000.9377490000001,65.728469000000004,15.228374618006088]
[1500,61.349710999999999,1500,1000.928454,44.776625000000003,22.353816394156549]
[1510,66.757616999999996,1510,1000.919179,38.234974999999999,26.178104706489282]
[1520,72.233346999999995,1520,1000.909846,35.351619999999997,28.31298384628484]
[1530,77.767382999999995,1530,1000.789191,32.326973000000002,30.958332875769095]
[1540,83.353050999999994,1540,1000.779418,29.214663999999999,34.256064625627729]
[1550,88.985681999999997,1550,1000.769632,26.339797000000001,37.994584088859909]
[1560,94.662062000000006,1560,1000.759759,23.819469000000002,42.014360563621295]
[1570,100.380047,1570,1000.749771,21.652493,46.21868581137516]
[1580,106.1383,1580,1000.739663,19.797039000000002,50.549966739975602]
[1590,111.93609600000001,1590,1000.7294439999999,18.203972,54.973136851671711]
[1600,117.77319300000001,1600,1000.7191330000001,16.828365999999999,59.466209197018898]
[1610,123.649728,1610,1000.708756,15.63241,64.015001909494444]
[1620,129.566148,1620,1000.6983310000001,14.585284,68.610136833811396]
[1630,135.52314899999999,1630,1000.687871,13.662146,73.24529184507324]
[1640,141.52164300000001,1640,1000.677378,12.842999000000001,77.916176587726895]
[1650,147.56271899999999,1650,1000.666846,12.111687999999999,82.61993258082606]
[1660,153.64762500000001,1660,1000.656262,11.455080000000001,87.354803458378285]
[1670,159.77774700000001,1670,1000.645608,10.862439999999999,92.119782295690484]
[1680,165.954598,1680,1000.634825,10.324935,96.914394618464911]
[1690,172.17980299999999,1690,1000.623735,9.8352520000000005,101.73849485503777]
[1700,178.45509799999999,1700,1000.612855,9.3872809999999998,106.59240465902747]
[1710,184.782319,1710,1000.6019250000001,8.9759010000000004,111.47648854415841]
[1720,191.1634,1720,1000.590948,8.5967889999999993,116.39124189275788]
[1730,197.60037299999999,1730,1000.579931,8.2462669999999996,121.33731917727137]
[1740,204.095361,1740,1000.568879,7.9211819999999999,126.31560277241452]
[1750,210.65058400000001,1750,1000.557788,7.6188219999999998,131.32709859870727]
[1760,217.26835700000001,1760,1000.54665,7.3368469999999997,136.37283835958416]
[1770,223.95108999999999,1770,1000.535452,7.0732299999999997,141.45382689379534]
[1780,230.701292,1780,1000.524182,6.8261969999999996,146.57124340243917]
[1790,237.52157199999999,1790,1000.51283,6.5941739999999998,151.72678640266395]
[1800,244.41464400000001,1800,1000.501397,6.3757380000000001,156.92322943634133]
[1810,251.383329,1810,1000.4898920000001,6.1696780000000002,162.16241625575921]
[1820,258.43056000000001,1820,1000.478338,5.9749930000000004,167.44426947445794]
[1830,265.55938500000002,1830,1000.4667920000001,5.7907469999999996,172.76990205236044]
[1840,272.77297600000003,1840,1000.437624,5.6160059999999996,178.14041224314934]
[1850,280.07463000000001,1850,1000.433507,5.4501010000000001,183.56237930269549]
[1860,287.46777900000001,1860,1000.421708,5.2923640000000001,189.03116036614261]
[1870,294.95599399999998,1870,1000.409932,5.1420880000000002,194.55324996382791]
[1880,302.54299200000003,1880,1000.398145,4.9986790000000001,200.13250400755879]
[1890,310.23264499999999,1890,1000.3863239999999,4.8617340000000002,205.7673916343428]
[1900,318.02899100000002,1900,1000.374449,4.7309299999999999,211.45407964184633]
[1910,325.93623600000001,1910,1000.3625060000001,4.6058139999999996,217.19559365619196]
[1920,333.95876900000002,1920,1000.350485,4.4859530000000003,222.99620281353816]
[1930,342.10117200000002,1930,1000.338388,4.3709809999999996,{"$f":"D198/E198","v":228.85901082617383}]
[1940,350.36822699999999,1940,1000.326221,4.2605829999999996,234.78623019431851]
[1950,358.76493299999998,1950,1000.313995,4.1544780000000001,240.77970686088599]
[1960,367.296513,1960,1000.30172,4.0524040000000001,246.84155873896088]
[1970,375.968435,1970,1000.289405,3.9541170000000001,252.97415453311066]
[1980,384.78641699999997,1980,1000.277051,3.8594050000000002,259.17908356339899]
[1990,393.75645200000002,1990,1000.2646580000001,3.768087,265.4568904592702]
[2000,402.884818,2000,1000.252853,3.680002,271.80769276755825]
[2010,412.17809699999998,2010,1000.23912,3.5949819999999999,278.23202452752196]
[2020,421.64319799999998,2020,1000.2265149999999,3.5128469999999998,284.73386828404426]
[2030,431.287374,2030,1000.21385,3.4333979999999999,291.31893535209144]
[2040,441.11824300000001,2040,1000.2011230000001,3.3563869999999998,297.99934363945522]
[2050,451.14381800000001,2050,1000.188339,3.2815409999999998,304.79227259388199]
[2060,461.372524,2060,1000.175507,3.208612,311.71594041286392]
[2070,471.81323500000002,2070,1000.162634,3.1374490000000002,318.78211693640276]
[2080,482.47529400000002,2080,1000.149725,3.0679989999999999,325.99414960695879]
[2090,493.36855200000002,2090,1000.1367739999999,3.0002629999999999,333.34970100954484]
[2100,504.503401,2100,1000.123774,2.9342410000000001,340.84581804971032]
[2110,515.89080899999999,2110,1000.110708,2.869901,348.48265079527135]
[2120,527.54236100000003,2120,1000.097561,2.807188,356.26312202816484]
[2130,539.47030199999995,2130,1000.0843159999999,2.7460499999999999,364.19013346443074]
[2140,551.68758300000002,2140,1000.070952,2.686445,372.26555987559772]
[2150,564.20791399999996,2150,1000.057413,2.6283539999999999,380.48809749371662]
[2160,577.04581199999996,2160,999.98565599999995,2.5715240000000001,388.86887931047886]
[2170,590.21666400000004,2170,999.97466699999995,2.5168029999999999,397.31940362435995]
[2180,603.73678800000005,2180,999.96124699999996,2.4641839999999999,405.79812505884303]
[2190,617.62349900000004,2190,999.94777099999999,2.4138269999999999,414.25825918758886]
[2200,631.89518299999997,2200,999.93424800000003,2.365491,422.71741807514803]
[2210,646.571371,2210,999.92068200000006,2.3186870000000002,431.24435596525103]
[2220,661.67282699999998,2220,999.90707299999997,2.2724530000000001,440.01221279383992]
[2230,677.221633,2230,999.893416,2.226299,449.12808926384099]
[2240,693.24128399999995,2240,999.87970700000005,2.180355,458.58573810228154]
[2250,709.75678800000003,2250,999.86594200000002,2.1348639999999999,468.35111838505878]
[2260,726.79477199999997,2260,999.85211700000002,2.09,478.39814210526322]
[2270,744.38359500000001,2270,999.83823500000005,2.0458609999999999,488.71269113590813]
[2280,762.55345699999998,2280,999.824296,2.0024769999999998,499.29377266255744]
[2290,781.33652600000005,2290,999.81030499999997,1.959835,510.15024479101555]
[2300,800.76705200000004,2300,999.79626499999995,1.917932,521.28869271694714]
[2310,820.88148799999999,2310,999.78218500000003,1.8767560000000001,532.71825692844459]
[2320,841.71860700000002,2320,999.76798299999996,1.836284,544.45172043104435]
[2330,863.31960300000003,2330,999.753737,1.7964789999999999,556.50733295518626]
[2340,885.72818700000005,2340,999.73948099999996,1.7573350000000001,568.89521975036052]
[2350,908.99064399999997,2350,999.72516499999995,1.7188159999999999,581.63594299797069]
[2360,933.15586099999996,2360,999.71078999999997,1.6808940000000001,594.74945475443417]
[2370,958.27530300000001,2370,999.69635800000003,1.643543,608.2568925790199]
[2380,984.40290000000005,2380,999.68186700000001,1.6067450000000001,622.17829649384316]
[2390,1011.59484,2390,999.66731700000003,1.5704800000000001,636.53616537619075]
[2400,1039.9092029999999,2400,999.65270699999996,1.5347280000000001,651.35496778582262]
[2410,1069.4054120000001,2410,999.63803600000006,1.4994670000000001,666.66224465093262]
[2420,1100.1433939999999,2420,999.62330299999996,1.4646790000000001,682.48626695678706]
[2430,1132.182395,2430,999.60850700000003,1.430348,698.85685651324013]
[2440,1165.5793200000001,2440,999.59364700000003,1.396458,715.80645246760025]
[2450,1200.3864229999999,2450,999.57872699999996,1.363,733.36663756419659]
[2460,1236.648181,2460,999.56374900000003,1.3299570000000001,751.57599005080613]
[2470,1274.397078,2470,999.54871400000002,1.2973170000000001,770.47376547135354]
[2480,1313.6479830000001,2480,999.53372200000001,1.2650680000000001,790.10276285543534]
[2490,1354.3907449999999,2490,999.51865199999997,1.233223,810.49303491744797]
[2500,1396.5805350000001,2500,999.50345200000004,1.201784,831.68310777976751]
[2510,1440.1254160000001,2510,999.48820999999998,1.170782,853.69283948677037]
[2520,1484.8705970000001,2520,999.47291700000005,1.140279,876.51611316177889]
[2530,1530.5788910000001,2530,999.45756800000004,1.1103810000000001,900.10326905809802]
[2540,1576.907105,2540,999.44215899999995,1.08125,924.33956901734098]
[2550,1623.3785829999999,2550,999.42669100000001,1.053191,948.95103642169374]
[2560,1669.3529840000001,2560,999.41116499999998,1.0266999999999999,973.42082886919263]
[2570,1713.9958549999999,2570,999.39558499999998,1.0024550000000001,{"$f":"D262/E262","v":996.94807746981155}]
[2580,1756.2526740000001,2580,999.37995699999999,0.98112500000000002,1018.6061480443368]
[2590,1794.8348149999999,2590,999.364284,0.96266399999999996,1038.1236693176436]
[2600,1828.2278670000001,2600,999.348567,0.94519799999999998,1057.2901836440619]
[2610,1854.7348549999999,2610,999.33280500000001,0.92547199999999996,1079.8087948635939]
[2620,1872.566329,2620,999.31699200000003,0.90132199999999996,1108.723621524827]
[2630,1879.9838050000001,2630,999.30111899999997,0.872977,1144.7049796271838]
[2640,1875.491059,2640,999.28296599999999,0.84216400000000002,1186.5657591632983]
[2650,1858.050632,2650,999.31014000000005,0.81023699999999999,1233.3553515823148]
[2660,1827.285983,2660,999.29432499999996,0.77858400000000005,1283.4765741397202]
[2670,1783.6220780000001,2670,999.27835600000003,0.74732299999999996,1337.1438534609533]
[2680,1728.3266180000001,2680,999.26228400000002,0.71656299999999995,1394.5211851574811]
[2690,1663.44058,2690,999.24612400000001,0.68634600000000001,1455.8926896929536]
[2700,1591.620236,2700,999.22988799999996,0.65673199999999998,1521.5185006973925]
[2710,1515.937817,2710,999.21358699999996,0.62786200000000003,1591.4541523455789]
[2720,1439.6933939999999,2720,999.19722999999999,0.59999599999999997,1665.3398189321263]
[2730,1366.2758799999999,2730,999.18082500000003,0.57347700000000001,1742.3206597649078]
[2740,1299.084357,2740,999.16437399999995,0.54857400000000001,1821.3848523626712]
[2750,1241.492851,2750,999.14787899999999,0.52525900000000003,1902.2003982797057]
[2760,1196.821148,2760,999.13133600000003,0.50310999999999995,1985.9103098725927]
[2770,1168.2697169999999,2770,999.11474199999998,0.48148299999999999,2075.0779196773301]
[2780,1158.797963,2780,999.09809399999995,0.45981699999999998,2172.8167814587109]
[2790,1170.974363,2790,999.08139400000005,0.437809,2282.0028688309285]
[2800,1206.883024,2800,999.06589199999996,0.41539799999999999,2405.0811318301967]
[2810,1268.187561,2810,999.04839700000002,0.39264500000000002,2544.4062626545606]
[2820,1356.403151,2820,999.03148199999998,0.36967800000000001,2702.4369370100467]
[2830,1473.3496210000001,2830,999.01452099999995,0.34663500000000003,2882.0359196272734]
[2840,1621.7248830000001,2840,998.99751400000002,0.323633,3086.8221534886738]
[2850,1805.7788969999999,2850,998.98046399999998,0.30075600000000002,3321.5645373658376]
[2860,2032.1599610000001,2860,998.96336599999995,0.27807799999999999,3592.3854673868482]
[2870,2311.1259399999999,2870,998.94621400000005,0.255685,3906.9410172673411]
[2880,2658.491802,2880,998.92900099999997,0.233679,4274.7914917472262]
[2890,3099.0259569999998,2890,998.91171899999995,0.212176,4707.9392532614429]
[2900,3672.7566489999999,2900,998.894364,0.19131699999999999,5221.1479586236455]
[2910,4447.3938079999998,2910,998.87693899999999,0.171316,5830.6109119988796]
[2920,5544.1849540000003,2920,998.85945300000003,0.15265699999999999,6543.1618137392989]
[2930,7192.7458960000004,2930,998.84192499999995,0.136132,7337.3044177709862]
[2940,9822.5114329999997,2940,998.82437800000002,0.122471,8155.5991050942675]
[2950,13823.227852,2950,998.80685000000005,0.112516,8877.0206015144522]
[2960,16292.117727000001,2960,998.78271199999995,0.107269,9311.0098164427745]
[2970,13044.344913000001,2970,998.78610000000003,0.10749599999999999,9291.3792141102931]
[2980,10850.428513999999,2980,998.76834099999996,0.113007,8838.1103913916832]
[2990,10146.074796999999,2990,998.75060199999996,0.123196,8107.0051138023955]
[3000,8124.690705,3000,998.73282099999994,0.137045,7287.6268451968326]
[3010,6493.6707450000004,3010,998.714967,0.15351799999999999,6505.5235672689851]
[3020,5390.5941990000001,3020,998.69702299999994,0.171822,5812.3931917915052]
[3030,4616.896874,3030,998.67898700000001,0.19147,5215.8509792656814]
[3040,4046.4277489999999,3040,998.66086800000005,0.21212700000000001,4707.8442065366498]
[3050,3608.1211480000002,3050,998.64268300000003,0.233546,4275.9999443364477]
[3060,3260.2740800000001,3060,998.62445300000002,0.25555099999999997,3907.73056258829]
[3070,2977.0285399999998,3070,998.60619499999996,0.27802100000000002,3591.8372892695152]
[3080,2741.54124,3080,998.58791599999995,0.300873,3318.9681892359899]
[3090,2542.3768359999999,3090,998.56961000000001,0.32405099999999998,3081.5199150750964]
[3100,2371.4983940000002,3100,998.55126399999995,0.34750799999999998,2873.462665607698]
[3110,2223.09076,3110,998.53286500000002,0.37120599999999998,2689.9696260297519]
[3120,2092.8410650000001,3120,998.51468899999998,0.39511600000000002,2527.1431402423591]
[3130,1977.4819500000001,3130,998.49615500000004,0.41923500000000002,2381.7099121018045]
[3140,1874.492041,3140,998.477487,0.44355,2251.1046939465673]
[3150,1781.8939210000001,3150,998.45874100000003,0.46806399999999998,2133.1671331270941]
[3160,1698.11447,3160,998.43994799999996,0.492784,2026.1208724309231]
[3170,1621.886186,3170,998.42113099999995,0.51771699999999998,1928.507526312638]
[3180,1552.1761059999999,3180,998.40230699999995,0.54285899999999998,1839.1558526247147]
[3190,1488.1337209999999,3190,998.38347199999998,0.56819600000000003,1757.1110532281114]
[3200,1429.0521960000001,3200,998.36460399999999,0.59371700000000005,1681.5496339164954]
[3210,1374.3391039999999,3210,998.34566700000005,0.61941500000000005,{"$f":"D326/E326","v":1611.7557162806841}]
[3220,1323.4940469999999,3220,998.32661499999995,0.64529300000000001,1547.0904147418303]
[3230,1276.0913390000001,3230,998.30741,0.67135800000000001,1486.9971162926486]
[3240,1231.7664769999999,3240,998.28803300000004,0.69760900000000003,1431.013695350834]
[3250,1190.205449,3250,998.26849300000003,0.72403300000000004,1378.7610412785052]
[3260,1151.1362180000001,3260,998.24883999999997,0.75063500000000005,1329.8724946212205]
[3270,1114.3218790000001,3270,998.22921099999996,0.77741499999999997,1284.0364682955692]
[3280,1079.5551149999999,3280,998.54244000000006,0.80530800000000002,1239.9509752790236]
[3290,1046.6536799999999,3290,998.52171999999996,0.83238599999999996,1199.5897576364812]
[3300,1015.456681,3300,998.50110299999994,0.85994199999999998,1161.1261026906466]
[3310,985.82151199999998,3310,998.48062700000003,0.88809199999999999,1124.2986391049576]
[3320,957.62129600000003,3320,998.46025599999996,0.91487499999999999,1091.3624877715536]
[3330,930.74275899999998,3330,998.43994499999997,0.93928800000000001,1062.9753015049696]
[3340,905.08442500000001,3340,998.41963999999996,0.96569700000000003,1033.8849970539413]
[3350,880.55511000000001,3350,998.39928799999996,0.99392899999999995,1004.4975928864134]
[3360,857.07262700000001,3360,998.37884599999995,1.022939,975.99059767982249]
[3370,834.56269499999996,3370,998.358296,1.0523690000000001,948.67702868480535]
[3380,812.95799299999999,3380,998.33763599999997,1.0821240000000001,922.57230779467034]
[3390,792.19735800000001,3390,998.31688599999995,1.112193,897.61119338100491]
[3400,772.22508500000004,3400,998.29607399999998,1.142579,873.72170677038525]
[3410,752.99032,3410,998.27522499999998,1.1732629999999999,850.85375146066997]
[3420,734.44654200000002,3420,998.25435500000003,1.2042189999999999,828.96412944821509]
[3430,716.55110000000002,3430,998.23347200000001,1.2354620000000001,807.98395418070322]
[3440,699.264815,3440,998.21181100000001,1.2670319999999999,787.83472793110207]
[3450,682.55162499999994,3450,998.19359499999996,1.2989790000000001,768.44475160876345]
[3460,666.37828200000001,3460,998.17260499999998,1.331305,749.77004142551857]
[3470,650.71407299999998,3470,998.15151300000002,1.3640479999999999,731.75688318886148]
[3480,635.53058299999998,3480,998.13032599999997,1.3972290000000001,714.36416364103513]
[3490,620.80147699999998,3490,998.10905600000001,1.4308590000000001,697.5593374329685]
[3500,606.50231499999995,3500,998.087717,1.4649479999999999,681.31272714116824]
[3510,592.61037699999997,3510,998.066328,1.499511,665.59453581867683]
[3520,579.104513,3520,998.04489999999998,1.5345629999999999,650.37727352998866]
[3530,565.96501000000001,3530,998.02343800000006,1.5701229999999999,635.63392039986684]
[3540,553.17346599999996,3540,998.00193899999999,1.6062110000000001,621.33925057168699]
[3550,540.71268499999996,3550,997.98039200000005,1.6428480000000001,607.46970626619134]
[3560,528.56657499999994,3560,997.95878800000003,1.68005,594.00540936281664]
[3570,516.72006099999999,3570,997.93711900000005,1.7178420000000001,580.92485746651903]
[3580,505.15900499999998,3580,997.91538700000001,1.7562519999999999,568.20740246843854]
[3590,493.87013300000001,3590,997.89361799999995,1.795304,555.83545627927083]
[3600,482.84096599999998,3600,997.87850700000001,1.8349930000000001,543.80507555069687]
[3610,472.05976800000002,3610,997.85546999999997,1.8753960000000001,532.07720929339723]
[3620,461.51548100000002,3620,997.83348599999999,1.9165289999999999,520.64617128151986]
[3630,451.19768599999998,3630,997.81147199999998,1.9584250000000001,509.49690286837637]
[3640,441.09655099999998,3640,997.78942099999995,2.0011130000000001,498.61723001149852]
[3650,431.20279099999999,3650,997.76732100000004,2.044635,487.9928794136851]
[3660,421.507632,3660,997.74516000000006,2.0890110000000002,477.61603936025227]
[3670,412.00277699999998,3670,997.72292600000003,2.1342279999999998,467.48656938246529]
[3680,402.68036999999998,3680,997.70061699999997,2.1802899999999998,457.59996009705134]
[3690,393.53297500000002,3690,997.67823699999997,2.2272370000000001,447.94435302574442]
[3700,384.55354,3700,997.65579700000001,2.2751700000000001,438.49725383158182]
[3710,375.73538100000002,3710,997.63330800000006,2.3242980000000002,429.21919134293449]
[3720,367.07215400000001,3720,997.61077899999998,2.3749120000000001,420.06220819971429]
[3730,358.557839,3730,997.58820900000001,2.4271419999999999,411.01353320077692]
[3740,350.18671799999998,3740,997.56558900000005,2.4809260000000002,402.09405238205409]
[3750,341.95335799999998,3750,997.54290300000002,2.5361069999999999,393.33628391862015]
[3760,333.8526,3760,997.51927000000001,2.592562,384.76197290556598]
[3770,325.87953599999997,3770,997.50942199999997,2.6503070000000002,376.37504711718299]
[3780,318.02950499999997,3780,997.48661800000002,2.7093250000000002,368.16794515239036]
[3790,310.29807499999998,3790,997.46369900000002,2.769749,360.12783071679058]
[3800,302.68103400000001,3800,997.44070099999999,2.8316659999999998,352.24518039910078]
[3810,295.17438299999998,3810,997.41764699999999,2.8951519999999999,344.51305043742093]
[3820,287.77432099999999,3820,997.39455699999996,2.9602849999999998,336.92518017690867]
[3830,280.47724599999998,3830,997.371441,3.0271400000000002,329.47648308304207]
[3840,273.27974,3840,997.348297,3.0957859999999999,322.16319118957188]
[3850,266.17857099999998,3850,997.32511799999997,3.1662979999999998,{"$f":"D390/E390","v":314.98144457660021}]
[3860,259.170681,3860,997.30188799999996,3.2387739999999998,307.92574227161265]
[3870,252.25318899999999,3870,997.278592,3.3133339999999998,300.98945412687044]
[3880,245.423385,3880,997.25522000000001,3.3901129999999999,294.16577559509079]
[3890,238.67872800000001,3890,997.23177299999998,3.46923,287.45046393580128]
[3900,232.01685000000001,3900,997.208259,3.5507689999999998,280.84289881994579]
[3910,225.435554,3910,997.18470500000001,3.6347779999999998,274.34542219634875]
[3920,218.932816,3920,997.16224,3.7212710000000002,267.9628116307573]
[3930,212.50679199999999,3930,997.13830299999995,3.8102659999999999,261.69781925986268]
[3940,206.155823,3940,997.11463700000002,3.901742,255.55627127575323]
[3950,199.878443,3950,997.09092499999997,3.9957220000000002,249.53961386703077]
[3960,193.67338899999999,3960,997.06715699999995,4.0923369999999997,243.64248521077323]
[3970,187.539614,3970,997.043316,4.1918220000000002,237.85440221459785]
[3980,181.47630899999999,3980,997.01938900000005,4.2943980000000002,232.16743976687769]
[3990,175.482913,3990,996.99537099999998,4.4002330000000001,226.57785871793607]
[4000,169.55914799999999,4000,996.971271,4.5095179999999999,221.08155927085778]
[4010,163.70504299999999,4010,996.94710899999995,4.6225430000000003,215.67070528062149]
[4020,157.920973,4020,996.92290600000001,4.7397200000000002,210.33371296194713]
[4030,152.20770099999999,4030,996.898685,4.8612919999999997,205.06867001611917]
[4040,146.56643399999999,4040,996.87445700000001,4.9865950000000003,199.91085239527172]
[4050,140.99888300000001,4050,996.85022300000003,5.1150399999999996,194.88610509399734]
[4060,135.50734600000001,4060,996.825963,5.2479170000000002,189.94697572389197]
[4070,130.094797,4070,996.80163900000002,5.3866269999999998,185.05117191147633]
[4080,124.765,4080,996.78051800000003,5.531968,180.18551770364544]
[4090,119.52264700000001,4090,996.73760200000004,5.6844320000000002,175.34515357031273]
[4100,114.37352,4100,996.71312599999999,5.8450990000000003,170.52117098444353]
[4110,109.324691,4110,996.68852500000003,6.0146300000000004,165.71069625230479]
[4120,104.38475699999999,4120,996.66382099999998,6.1939469999999996,160.90932340880542]
[4130,99.564116999999996,4130,996.63903100000005,6.3840870000000001,156.11300895492184]
[4140,94.875309999999999,4140,996.61417100000006,6.5862340000000001,151.31775928398537]
[4150,90.333386000000004,4150,996.58925299999999,6.8016649999999998,146.52136690060448]
[4160,85.956335999999993,4160,996.56428200000005,7.0317800000000004,141.72290401576842]
[4170,81.765551000000002,4170,996.53925800000002,7.278149,136.92207428015007]
[4180,77.786272999999994,4180,996.51418000000001,7.5425449999999996,132.11908977672655]
[4190,74.047994000000003,4190,996.48904600000003,7.8269890000000002,127.31448146918311]
[4200,70.584684999999993,4200,996.46385599999996,8.1337949999999992,122.50909397151023]
[4210,67.434719000000001,4210,996.43861300000003,8.4656289999999998,117.70402565479777]
[4220,64.640276999999998,4220,996.41332199999999,8.8255859999999995,112.9005283048627]
[4230,62.246026000000001,4230,996.38798799999995,9.2172999999999998,108.09976761090557]
[4240,60.296881999999997,4240,996.362122,9.6450689999999994,103.30274692695305]
[4250,58.834819000000003,4250,996.33752400000003,10.114012000000001,98.510613196820401]
[4260,57.895007,4260,996.31206299999997,10.630267,93.724086422288352]
[4270,57.501871999999999,4270,996.28652099999999,11.201282000000001,88.943972752404576]
[4280,57.665979999999998,4280,996.260898,11.836164999999999,84.170920057298972]
[4290,58.382576999999998,4290,996.23519399999998,12.54617,79.405523279215885]
[4300,59.632241999999998,4300,996.20941900000003,13.345362,74.648362404856456]
[4310,61.383431999999999,4310,996.18359099999998,14.25155,69.900017261280354]
[4320,63.596212999999999,4320,996.15772800000002,15.287599,65.161162848397581]
[4330,66.226247999999998,4330,996.13184799999999,16.4833,60.432792462674342]
[4340,69.228308999999996,4340,996.10595699999999,17.878108999999998,55.716516606985678]
[4350,72.558893999999995,4350,996.08004600000004,19.525206000000001,51.015085116131424]
[4360,76.177901000000006,4360,996.05408899999998,21.497599000000001,46.333271403936777]
[4370,80.049477999999993,4370,996.02803900000004,23.897341000000001,41.679450404126548]
[4380,84.142278000000005,4380,996.00182600000005,26.869033000000002,37.068763360408241]
[4390,88.429327000000001,4390,995.97528199999999,30.617553999999998,32.529550923630282]
[4400,92.887674000000004,4400,996.20862899999997,35.421385000000001,28.12449679762663]
[4410,97.497956000000002,4410,996.17763000000002,41.598599999999998,23.947383565793082]
[4420,102.243926,4420,996.15073800000005,49.220208999999997,20.238653151594704]
[4430,107.112016,4430,996.12353399999995,57.009078000000002,17.473068657591689]
[4440,112.090934,4440,996.09610999999995,60.433705000000003,16.482459746593392]
[4450,117.171314,4450,996.06873700000006,54.764715000000002,18.188147916044116]
[4460,122.345418,4460,996.04158600000005,43.209681000000003,23.051352450391846]
[4470,127.60687799999999,4470,996.01454100000001,31.557110000000002,31.562286312022866]
[4480,132.95048299999999,4480,995.98748699999999,21.696712999999999,45.904994318724683]
[4490,138.372006,4490,995.96038099999998,13.360151999999999,{"$f":"D454/E454","v":74.54708456909772}]
[4500,143.86805200000001,4500,995.93319599999995,5.9635449999999999,167.00355174648635]
[4510,149.435937,4510,995.90590999999995,0.80545199999999995,1236.4559402670798]
[4520,155.073587,4520,995.87850400000002,6.7954280000000002,146.55125534403425]
[4530,160.77945099999999,4530,995.85097399999995,11.515496000000001,86.479208016745432]
[4540,166.55243300000001,4540,995.82334500000002,14.574107,68.328258122435912]
[4550,172.39183399999999,4550,995.79564600000003,16.067943,61.974058907229136]
[4560,178.297304,4560,995.76746000000003,16.444288,60.554002702944636]
[4570,184.268798,4570,995.74083900000005,16.168759999999999,61.584242638272826]
[4580,190.306546,4580,995.71307200000001,15.568611000000001,63.956448780176984]
[4590,196.411022,4590,995.68525699999998,14.834978,67.117407049744187]
[4600,202.58292399999999,4600,995.65738699999997,14.068967000000001,70.769757793873566]
[4610,208.82315,4610,995.629458,13.320454,74.744408711594971]
[4620,215.13278600000001,4620,995.60146499999996,12.612019,78.94068863993941]
[4630,221.51308700000001,4630,995.57341199999996,11.952192,83.296303473036573]
[4640,227.965473,4640,995.54530399999999,11.34247,87.771473409230964]
[4650,234.491513,4650,995.51714600000003,10.780984,92.340100495464981]
[4660,241.092918,4660,995.48894399999995,10.264393,96.984687160750752]
[4670,247.77154200000001,4670,995.46070099999997,9.7888529999999996,101.69329348392503]
[4680,254.52936500000001,4680,995.43241699999999,9.3504900000000006,106.45778103607404]
[4690,261.36850099999998,4690,995.404089,8.9456330000000008,111.27262754910691]
[4700,268.29118599999998,4700,995.37571800000001,8.5709169999999997,116.1340983701044]
[4710,275.29978,4710,995.34731599999998,8.2233079999999994,121.03977085620532]
[4720,282.39676400000002,4720,995.32474300000001,7.9001099999999997,125.98871952415853]
[4730,289.58474100000001,4730,995.29518299999995,7.5988420000000003,130.9798496928874]
[4740,296.86642999999998,4740,995.26657299999999,7.3173849999999998,136.01396851470847]
[4750,304.24467099999998,4750,995.23789999999997,7.053871,141.09102647326552]
[4760,311.72242299999999,4760,995.20916599999998,6.8066760000000004,146.21074456900843]
[4770,319.30276500000002,4770,995.18037100000004,6.5743830000000001,151.37243616625318]
[4780,326.98889300000002,4780,995.15151300000002,6.3557560000000004,156.57484538424697]
[4790,334.78412500000002,4790,995.12258999999995,6.1496190000000004,161.8185760776399]
[4800,342.69189699999998,4800,995.09360300000003,5.9548670000000001,167.10593250865216]
[4810,350.71576900000002,4810,995.06455800000003,5.7705159999999998,172.43944181074968]
[4820,358.859419,4820,995.03545999999994,5.595688,177.82182637773943]
[4830,367.12664599999999,4830,995.00631299999998,5.4296170000000004,183.25534066214982]
[4840,375.52136899999999,4840,994.97711900000002,5.2716609999999999,188.74072498212612]
[4850,384.04762599999998,4850,994.94787499999995,5.121264,194.27779450541897]
[4860,392.70957199999998,4860,994.91857300000004,4.977887,199.86764926564223]
[4870,401.51147900000001,4870,994.88919999999996,4.8410380000000002,205.51154525124568]
[4880,410.45772799999997,4880,994.86066700000003,4.7102579999999996,211.21150200265041]
[4890,419.55280900000002,4890,994.82642199999998,4.5851519999999999,216.96694504347948]
[4900,428.801311,4900,994.79680599999995,4.4652450000000004,222.78661215677971]
[4910,438.207919,4910,994.76715300000001,4.3502289999999997,228.67006610456602]
[4920,447.777402,4920,994.73746400000005,4.2397900000000002,234.61951275888666]
[4930,457.51459799999998,4930,994.70774500000005,4.1336339999999998,240.63759515235265]
[4940,467.42440800000003,4940,994.67800199999999,4.0314880000000004,246.72726348187069]
[4950,477.51177000000001,4950,994.64823100000001,3.9331079999999998,252.89115656117249]
[4960,487.78164099999998,4960,994.61842000000001,3.8382710000000002,259.13189037459836]
[4970,498.23897299999999,4970,994.58855200000005,3.7467670000000002,265.45246928885621]
[4980,508.88867800000003,4980,994.55861100000004,3.6583999999999999,271.85616963699982]
[4990,519.73559699999998,4990,994.52858900000001,3.5729929999999999,278.34607820390357]
[5000,530.78445099999999,5000,994.49848499999996,3.4903870000000001,284.92499112562587]
[5010,542.03979400000003,5010,994.46831299999997,3.4104450000000002,291.59488365887734]
[5020,553.50595399999997,5020,994.43808799999999,3.3330500000000001,298.3567867268718]
[5030,565.18695500000001,5030,994.40782799999999,3.2580960000000001,305.21133447264907]
[5040,577.08644500000003,5040,994.37625000000003,3.1854749999999998,312.15948955807221]
[5050,589.20759399999997,5050,994.34643000000005,3.1150730000000002,319.2048565154011]
[5060,601.55298000000005,5060,994.31612299999995,3.0467200000000001,326.35625295399637]
[5070,614.12446899999998,5070,994.28574100000003,2.9801489999999999,333.63625140890611]
[5080,626.92305399999998,5080,994.25526400000001,2.9150700000000001,341.07423286576307]
[5090,639.94869300000005,5090,994.22467400000005,2.85134,348.68681882904178]
[5100,653.20010400000001,5100,994.19397500000002,2.7889849999999998,356.47161063971305]
[5110,666.67454099999998,5110,994.16319099999998,2.728056,364.42184141381261]
[5120,680.36753799999997,5120,994.13236400000005,2.6685560000000002,372.53569496012074]
[5130,694.27260999999999,5130,994.10154,2.6105170000000002,{"$f":"D518/E518","v":380.80638432923439}]
[5140,708.38092600000004,5140,994.07075599999996,2.5542400000000001,389.18455430969681]
[5150,722.68093299999998,5150,994.04002100000002,2.5006249999999999,397.51662924268936]
[5160,737.15794000000005,5160,994.00930700000004,2.4503439999999999,405.66112635613615]
[5170,751.79365700000005,5170,993.97854099999995,2.4014069999999998,413.91506770822275]
[5180,766.56568100000004,5180,993.94760199999996,2.352036,422.59030133892509]
[5190,781.44694900000002,5190,993.91629799999998,2.3027310000000001,431.62501308229224]
[5200,796.40513399999998,5200,993.88795200000004,2.254121,440.92040844302505]
[5210,811.40201999999999,5210,991.65909299999998,2.2158419999999999,447.53149953832451]
[5220,826.39284099999998,5220,991.62468699999999,2.1692990000000001,457.11756977714919]
[5230,841.32561699999997,5230,991.58948599999997,2.1237119999999998,466.91335077449298]
[5240,856.14050199999997,5240,991.55393600000002,2.0790470000000001,476.92713825132381]
[5250,870.76917300000002,5250,991.51821900000004,2.035247,487.17340892776161]
[5260,885.13430000000005,5260,991.48245299999996,1.992273,497.66395117536604]
[5270,899.14914199999998,5270,991.44671000000005,1.950102,508.40761662723287]
[5280,912.71733800000004,5280,991.41101700000002,1.908703,519.41607311352266]
[5290,925.73293899999999,5290,991.37536299999999,1.868042,530.70293012683874]
[5300,938.08077400000002,5300,991.33970999999997,1.828087,542.28256642052588]
[5310,949.63722499999994,5310,991.30400699999996,1.7888090000000001,554.16984541110867]
[5320,960.27148099999999,5320,991.26821099999995,1.7501910000000001,566.37716169263808]
[5330,969.84735499999999,5330,991.23229800000001,1.7122189999999999,578.91677291281087]
[5340,978.22570299999995,5340,991.19626300000004,1.6748730000000001,591.80383408174828]
[5350,985.26748399999997,5350,991.16012000000001,1.6381289999999999,605.05620741712039]
[5360,990.83743400000003,5360,991.12302899999997,1.6019570000000001,618.69515161767754]
[5370,994.80829300000005,5370,991.08728499999995,1.566344,632.73922267394641]
[5380,997.06546700000001,5380,991.05103899999995,1.531261,647.21235569899579]
[5390,997.511931,5390,991.01477399999999,1.496688,662.13851784740712]
[5400,996.07314799999995,5400,990.97847899999999,1.4626079999999999,677.54208851585668]
[5410,992.70172500000001,5410,990.94213400000001,1.4290080000000001,693.44757622070688]
[5420,987.38151500000004,5420,990.90572099999997,1.3958759999999999,709.8809070433191]
[5430,980.13089500000001,5430,990.86922900000002,1.363191,726.87483192010507]
[5440,971.00499400000001,5440,990.83265700000004,1.330937,744.46247793847499]
[5450,960.09673399999997,5450,990.79601500000001,1.299102,762.67761499866833]
[5460,947.53662699999995,5460,990.75931500000002,1.2676829999999999,781.55131448477266]
[5470,933.49140299999999,5470,990.72256300000004,1.236675,801.11796793822145]
[5480,918.16164600000002,5480,990.68576099999996,1.206051,821.42940970157974]
[5490,901.77866300000005,5490,990.64889700000003,1.1757569999999999,842.56261880643717]
[5500,884.60091799999998,5500,990.61195299999997,1.1457900000000001,864.56676441581783]
[5510,866.91028900000003,5510,990.57490099999995,1.1161700000000001,887.47672935126354]
[5520,849.00846000000001,5520,990.54654600000003,1.086965,911.29571421342916]
[5530,831.21360000000004,5530,990.50549000000001,1.0580480000000001,936.16309468001441]
[5540,813.85746800000004,5540,990.46824600000002,1.029488,962.0979030352953]
[5550,797.28289700000005,5550,990.43092000000001,1.0012080000000001,989.23592300500991]
[5560,781.84156800000005,5560,990.39355799999998,0.97292999999999996,1017.9494496006907]
[5570,767.89184799999998,5570,990.35618399999998,0.94446399999999997,1048.5907181216012]
[5580,755.79644199999996,5580,990.318806,0.91620000000000001,1080.8980637415411]
[5590,745.91961500000002,5590,990.28141700000003,0.88841199999999998,1114.6646116891714]
[5600,738.62381500000004,5600,990.24399500000004,0.86106199999999999,1150.0263569870694]
[5610,734.26570700000002,5610,990.20651199999998,0.83407200000000004,1187.1954843226963]
[5620,733.19189300000005,5620,990.16894400000001,0.80740299999999998,1226.3627259249718]
[5630,735.73483999999996,5630,990.13127899999995,0.78103800000000001,1267.7120434601134]
[5640,742.20983899999999,5640,990.09351700000002,0.75496600000000003,1311.4412000010595]
[5650,752.91392499999995,5650,990.05567399999995,0.72916000000000003,1357.8030528279114]
[5660,768.12766799999997,5660,990.01776900000004,0.70360299999999998,1407.0687148860936]
[5670,788.12055299999997,5670,989.97982000000002,0.67832999999999999,1459.4368817537188]
[5680,813.16027699999995,5680,989.94210499999997,0.65343099999999998,1514.9910319528765]
[5690,843.52601500000003,5690,989.90308600000003,0.62902599999999997,1573.7077418103545]
[5700,879.52541699999995,5700,989.86504100000002,0.60521199999999997,1635.5674391783375]
[5710,921.515131,5710,989.826956,0.58207699999999996,1700.5086199935749]
[5720,969.92488300000002,5720,989.78880000000004,0.55959400000000004,1768.7623527057117]
[5730,1025.2855910000001,5730,989.75055999999995,0.53757699999999997,1841.1326377430582]
[5740,1088.2627279999999,5740,989.71223599999996,0.51570000000000005,1919.1627612953264]
[5750,1159.6970060000001,5750,989.67383800000005,0.49363600000000002,2004.8656054258604]
[5760,1240.655665,5760,989.63538700000004,0.47120400000000001,2100.2270502797091]
[5770,1332.4992709999999,5770,989.596901,0.44839899999999999,{"$f":"D582/E582","v":2206.9560837557624}]
[5780,1436.9712830000001,5780,989.55839400000002,0.425319,2326.6263533959218]
[5790,1556.3212900000001,5790,989.51986599999998,0.40208700000000003,2460.9596082439866]
[5800,1693.47848,5800,989.48130600000002,0.37879600000000002,2612.174642815658]
[5810,1852.3011859999999,5810,989.44269099999997,0.35551700000000003,2783.1093618589261]
[5820,2037.9435089999999,5820,989.40399100000002,0.33232299999999998,2977.2359752409557]
[5830,2257.4055250000001,5830,989.36515899999995,0.30933300000000002,3198.3821932997766]
[5840,2520.3761100000002,5840,989.30675599999995,0.28672399999999998,3450.3800030691536]
[5850,2840.5474789999998,5850,989.26890700000001,0.26546199999999998,3726.5932864214092]
[5860,3237.6855860000001,5860,989.22997299999997,0.24682000000000001,4007.900384895875]
[5870,3740.8482909999998,5870,989.190967,0.232514,4254.3286296739125]
[5880,4392.9823660000002,5880,989.15191000000004,0.22323000000000001,4431.0886081619856]
[5890,5255.2369189999999,5890,989.11281299999996,0.217667,4544.1560411086657]
[5900,6398.793498,5900,989.07367699999998,0.213675,4628.8694372294367]
[5910,7827.0939470000003,5910,989.034492,0.21018300000000001,4705.5874737728545]
[5920,9178.6853499999997,5920,988.99524399999996,0.207402,4768.4942478857483]
[5930,9461.9082579999995,5930,988.95592299999998,0.20598900000000001,4801.0132725533886]
[5940,8311.3241589999998,5940,988.91652399999998,0.206536,4788.1072742766391]
[5950,6796.8697910000001,5950,988.87705100000005,0.20940600000000001,4722.2956887577238]
[5960,5880.0916520000001,5960,988.83751500000005,0.21471199999999999,4605.4133676739075]
[5970,6007.1476890000004,5970,988.79792999999995,0.22237999999999999,4446.4337170608869]
[5980,6324.0012189999998,5980,988.75830900000005,0.23225599999999999,4257.1916721204188]
[5990,5743.8037619999996,5990,988.71865600000001,0.24412200000000001,4050.1005890497372]
[6000,4907.3793159999996,6000,988.67995800000006,0.25773299999999999,3836.0627393465334]
[6010,4217.2363759999998,6010,988.63475000000005,0.27283499999999999,3623.5627760367993]
[6020,3690.6427570000001,6020,988.59488299999998,0.28926600000000002,3417.5979306244076]
[6030,3284.306544,6030,988.55497300000002,0.30680800000000003,3222.0638738233683]
[6040,2962.5915190000001,6040,988.51499899999999,0.325299,3038.7889264953164]
[6050,2701.473962,6050,988.47496000000001,0.344609,2868.3956600088795]
[6060,2484.9933390000001,6060,988.43486399999995,0.36463099999999998,2710.781211690723]
[6070,2302.3082009999998,6070,988.394721,0.38527600000000001,2565.4199093636771]
[6080,2145.8368380000002,6080,988.35454000000004,0.406468,2431.567897103831]
[6090,2010.1254160000001,6090,988.31432099999995,0.428147,2308.3527877107626]
[6100,1891.1500309999999,6100,988.27405899999997,0.450266,2194.8671651868008]
[6110,1785.875002,6110,988.23374100000001,0.47278500000000001,2090.2392017513243]
[6120,1691.9652599999999,6120,988.193352,0.495672,1993.6436837263352]
[6130,1607.593869,6130,988.15288099999998,0.51889700000000005,1904.3333860091693]
[6140,1531.3099420000001,6140,988.11231999999995,0.54243399999999997,1821.6268154282363]
[6150,1461.945921,6150,988.07166099999995,0.56627000000000005,1744.8772864534583]
[6160,1398.5511300000001,6160,988.02780099999995,0.59041299999999997,1673.4519751428238]
[6170,1340.3433010000001,6170,987.98788200000001,0.61483500000000002,1606.9154846422211]
[6180,1286.672609,6180,987.94711600000005,0.63955200000000001,1544.7486928349845]
[6190,1236.994592,6190,987.90632400000004,0.66458099999999998,1486.5100326371053]
[6200,1190.8494929999999,6200,987.865497,0.68993400000000005,1431.8260833644956]
[6210,1147.846299,6210,987.82462399999997,0.71560000000000001,1380.4145108999439]
[6220,1107.6502760000001,6220,987.78368699999999,0.74157799999999996,1332.0024151201897]
[6230,1069.973131,6230,987.74267099999997,0.76788999999999996,1286.3075062834521]
[6240,1034.565182,6240,987.70156899999995,0.79454899999999995,1243.0971142119618]
[6250,1001.209061,6250,987.66038300000002,0.82150900000000004,1202.2514458149576]
[6260,969.71461999999997,6260,987.61912700000005,0.84848500000000004,1163.9794775393791]
[6270,939.91477299999997,6270,987.57782499999996,0.87436100000000005,1129.4852183480277]
[6280,911.66207999999995,6280,987.53650000000005,0.89803299999999997,1099.666159261408]
[6290,884.82592199999999,6290,987.49517400000002,0.92361400000000005,1069.1643630347742]
[6300,859.29015900000002,6300,987.45386099999996,0.95126100000000002,1038.0472457085909]
[6310,834.95115499999997,6310,987.41257199999995,0.97903300000000004,1008.5590291644918]
[6320,811.71613600000001,6320,987.37117599999999,1.006937,980.56896906161955]
[6330,789.50179100000003,6330,987.27650500000004,1.0351490000000001,953.75303941751372]
[6340,768.23308599999996,6340,987.23485900000003,1.0638939999999999,927.94475671448481]
[6350,747.84225200000003,6350,987.19317899999999,1.0930550000000001,903.15050843736128]
[6360,728.26792499999999,6360,987.15142200000003,1.12262,879.32819832178302]
[6370,709.45439599999997,6370,987.10957399999995,1.15259,856.42732801776867]
[6380,691.35097299999995,6380,987.067635,1.182958,834.40632296328363]
[6390,673.91142200000002,6390,987.02561200000002,1.2137260000000001,813.21946798536078]
[6400,657.09348599999998,6400,986.98351300000002,1.2449060000000001,792.81770109550439]
[6410,640.85845900000004,6410,986.94135000000006,1.2765040000000001,{"$f":"D646/E646","v":773.15962190482753}]
[6420,625.17082500000004,6420,986.89913000000001,1.308513,754.21423401983782]
[6430,609.997927,6430,986.85685899999999,1.3409169999999999,735.9567064926465]
[6440,595.30968600000006,6440,986.81453899999997,1.373696,718.36457192857802]
[6450,581.07835,6450,986.77216899999996,1.406849,701.4058857773648]
[6460,567.27827200000002,6460,986.72974499999998,1.440396,685.04060341739353]
[6470,553.88571300000001,6470,986.68726000000004,1.474369,669.22680821422591]
[6480,540.87866799999995,6480,986.64464999999996,1.5088060000000001,653.92412941093812]
[6490,528.23670700000002,6490,986.60178099999996,1.5437270000000001,639.10379296339306]
[6500,515.94084299999997,6500,986.55910900000003,1.5791660000000001,624.7342641622223]
[6510,503.97340200000002,6510,986.51638800000001,1.615138,610.79386900685893]
[6520,492.31791099999998,6520,986.473614,1.651656,597.26336113573291]
[6530,480.959003,6530,986.430789,1.6887270000000001,584.12685354115854]
[6540,469.88232499999998,6540,986.38791400000002,1.726369,571.36563156544173]
[6550,459.074456,6550,986.34499300000004,1.764602,558.96173358071678]
[6560,448.52283699999998,6560,986.30202399999996,1.803442,546.89977498583266]
[6570,438.21570000000003,6570,986.25900200000001,1.8428990000000001,535.16714806400137]
[6580,428.14201500000001,6580,986.21591999999998,1.882984,523.75161976947231]
[6590,418.29143199999999,6590,986.17277100000001,1.9237310000000001,512.63548333940662]
[6600,408.65423399999997,6600,986.129549,1.9652259999999999,501.7893865641916]
[6610,399.22129100000001,6610,986.08625600000005,2.0075159999999999,491.19720888899519]
[6620,389.98402199999998,6620,986.04290700000001,2.050548,480.86799577478803]
[6630,380.93435799999997,6630,985.999549,2.0943040000000002,470.80058530184726]
[6640,372.06470999999999,6640,985.94126700000004,2.1388560000000001,460.96664151303315]
[6650,363.36793699999998,6650,985.90664100000004,2.1841919999999999,451.38277266833688]
[6660,354.83732099999997,6660,985.86301100000003,2.2302810000000002,442.03533590610328]
[6670,346.466542,6670,985.81941099999995,2.2772260000000002,432.90363407057527]
[6680,338.24965600000002,6680,985.77581299999997,2.3250959999999998,423.9720910448429]
[6690,330.18107500000002,6690,985.73219300000005,2.3738630000000001,415.24392646079406]
[6700,322.25555200000002,6700,985.68852900000002,2.4234279999999999,406.73316021767516]
[6710,314.46816100000001,6710,985.64479700000004,2.473821,398.43011964083092]
[6720,306.81428699999998,6720,985.60098200000004,2.5251139999999999,390.31940023301922]
[6730,299.28961099999998,6730,985.55707900000004,2.577353,382.39118933262154]
[6740,291.89010400000001,6740,985.51309400000002,2.6305749999999999,374.63790007888014]
[6750,284.61201299999999,6750,985.46904300000006,2.6848100000000001,367.05355053057758]
[6760,277.45185900000001,6760,985.42494299999998,2.7400959999999999,359.63153955189892]
[6770,270.40642800000001,6770,985.380809,2.7964799999999999,352.3646902534615]
[6780,263.47277300000002,6780,985.33665099999996,2.8540100000000002,345.24639051720209]
[6790,256.64820300000002,6790,985.29246599999999,2.912725,338.27170982499206]
[6800,249.930294,6800,985.24888199999998,2.972664,331.43634194782862]
[6810,243.31688199999999,6810,985.20342600000004,3.0338799999999999,324.73381478502779]
[6820,236.80607000000001,6820,985.15903100000003,3.0964529999999999,318.15726930135872]
[6830,230.39623599999999,6830,985.11456399999997,3.1604730000000001,311.69845905976729]
[6840,224.08603600000001,6840,985.070021,3.22607,305.34675967973419]
[6850,217.87441999999999,6850,985.02541399999996,3.2934139999999998,299.08945975209917]
[6860,211.76064099999999,6860,984.98076000000003,3.3626870000000002,292.91479105846008]
[6870,205.744272,6870,984.93607399999996,3.434053,286.81446500680102]
[6880,199.82522700000001,6880,984.89136599999995,3.507644,280.78430023115232]
[6890,194.003781,6890,984.846632,3.5835759999999999,274.8223093357027]
[6900,188.280596,6900,984.80185700000004,3.6619730000000001,268.92657510036258]
[6910,182.65675300000001,6910,984.75701900000001,3.7429869999999998,263.09389239129069]
[6920,177.13378800000001,6920,984.71208799999999,3.826797,257.32017872910427]
[6930,171.71372700000001,6930,984.66704100000004,3.9135909999999998,251.601927999119]
[6940,166.399135,6940,984.62185199999999,4.003571,245.93590372195223]
[6950,161.19316499999999,6950,984.57645600000001,4.0969600000000002,240.3187866125127]
[6960,156.099614,6960,984.44761000000005,4.1944549999999996,234.70215081577945]
[6970,151.122983,6970,984.40503000000001,4.2952329999999996,229.18547841292897]
[6980,146.26854599999999,6980,984.35986000000003,4.3999069999999998,223.72287868811773]
[6990,141.54241999999999,6990,984.31464100000005,4.5087380000000001,218.31267219341643]
[7000,136.951638,7000,984.26938399999995,4.6221050000000004,212.94829606856612]
[7010,132.50422499999999,7010,984.22408800000005,4.7399459999999998,207.64457822937226]
[7020,128.209271,7020,984.17874600000005,4.8630560000000003,202.37865778226694]
[7030,124.07699599999999,7030,984.13334899999995,4.9925030000000001,197.12223487897754]
[7040,120.11879999999999,7040,984.08789100000001,5.1288,191.874881258774]
[7050,116.34729400000001,7050,984.04236900000001,5.2723509999999996,{"$f":"D710/E710","v":186.6420443176109}]
[7060,112.776293,7060,983.99678900000004,5.4236170000000001,181.42814822654327]
[7070,109.420766,7070,983.95115699999997,5.5831540000000004,176.2357185562139]
[7080,106.296723,7080,983.90548100000001,5.7516189999999998,171.065830507897]
[7090,103.421025,7090,983.85976400000004,5.9297810000000002,165.91839799817228]
[7100,100.811098,7100,983.81400499999995,6.1184890000000003,160.79362159513565]
[7110,98.484555999999998,7110,983.76820599999996,6.3186939999999998,155.69169926570268]
[7120,96.458709999999996,7120,983.72229200000004,6.5314810000000003,150.61244027196895]
[7130,94.749988999999999,7130,983.67635099999995,6.7580929999999997,145.5553143468135]
[7140,93.373294000000001,7140,983.63034800000003,6.9999330000000004,140.5199661196757]
[7150,92.341324999999998,7150,983.58427800000004,7.2586069999999996,135.5059280658121]
[7160,91.663943000000003,7160,983.53815199999997,7.5359619999999996,130.51262095005256]
[7170,91.347627000000003,7170,983.49197600000002,7.8341200000000004,125.53955977186972]
[7180,91.395088000000001,7180,983.44575599999996,8.1555300000000006,120.58636973930571]
[7190,91.805098000000001,7190,983.39949100000001,8.5030380000000001,115.6527221211995]
[7200,92.572542999999996,7200,983.35317499999996,8.8799720000000004,110.73831933253842]
[7210,93.688694999999996,7210,983.30679799999996,9.2902450000000005,105.84293503562068]
[7220,95.141687000000005,7220,983.26035000000002,9.7384850000000007,100.96645936200548]
[7230,96.917102,7230,983.21382600000004,10.230197,96.10898265204473]
[7240,98.998641000000006,7240,983.16722600000003,10.771971000000001,91.270875682825363]
[7250,101.36879,7250,983.12055899999996,11.371744,86.45292744894715]
[7260,104.009443,7260,983.07383500000003,12.039149999999999,81.656415527674298]
[7270,106.902439,7270,983.02706599999999,12.785947999999999,76.88339308121698]
[7280,110.03000299999999,7280,982.98041599999999,13.626575000000001,72.137012859063987]
[7290,113.375079,7290,982.93365100000005,14.578749999999999,67.422354522850043]
[7300,116.921567,7300,982.886754,15.664361,62.7466868262293]
[7310,120.654473,7310,982.83981200000005,16.910216999999999,58.121064442874982]
[7320,124.559988,7320,982.79280700000004,18.348645999999999,53.562143331993006]
[7330,128.62550999999999,7330,982.74572499999999,20.017123999999999,49.095250896182691]
[7340,132.83963199999999,7340,982.69856100000004,21.955245000000001,44.759170804060716]
[7350,137.192094,7350,982.65131699999995,24.194865,40.614044219713563]
[7360,141.673722,7360,982.60399399999994,26.734905999999999,36.753598235954151]
[7370,146.276354,7370,982.55659600000001,29.485935000000001,33.322890930879417]
[7380,150.99276,7380,982.50912000000005,32.171830999999997,30.539421893643546]
[7390,155.816564,7390,982.46156800000006,34.226725999999999,28.704514945425984]
[7400,160.74216799999999,7400,982.41396699999996,34.869045,28.174386967007557]
[7410,165.76467600000001,7410,982.36636299999998,33.563403000000001,29.268973798634182]
[7420,170.87982600000001,7420,982.31878400000005,30.528254,32.177365400589238]
[7430,176.08392900000001,7430,982.27121299999999,26.563858,36.97773166081523]
[7440,181.373808,7440,982.22153000000003,22.432245999999999,43.786142947968742]
[7450,186.746745,7450,982.20710999999994,18.54748,52.956364422552276]
[7460,192.20043699999999,7460,982.15960199999995,15.036042999999999,65.320350706632055]
[7470,197.73294999999999,7470,982.11196399999994,11.878811000000001,82.677631961650022]
[7480,203.342682,7480,982.06424400000003,9.0102519999999995,108.99409295100737]
[7490,209.02832900000001,7490,982.01645199999996,6.3783139999999996,153.9617604275989]
[7500,214.78885,7500,981.96858999999995,4.0299659999999999,243.66671828000534]
[7510,220.623447,7510,981.92065000000002,2.4919259999999999,394.04085434318677]
[7520,226.531531,7520,981.87262299999998,3.1224889999999998,314.45190775692083]
[7530,232.51270700000001,7530,981.82450300000005,5.0524420000000001,194.32672418604707]
[7540,238.56674699999999,7540,981.77629200000001,7.0933390000000003,138.40820127164372]
[7550,244.69357500000001,7550,981.72799999999995,8.8642599999999998,110.75126406490784]
[7560,250.893249,7560,981.67964900000004,10.197696000000001,96.264847373367473]
[7570,257.16594500000002,7570,981.631259,11.049274,88.841245044697047]
[7580,263.51193899999998,7580,981.58284500000002,11.470326,85.575845446764106]
[7590,269.93159800000001,7590,981.53441399999997,11.56099,84.900550385390872]
[7600,276.425363,7600,981.48727399999996,11.426092000000001,85.898772213631744]
[7610,282.99373500000002,7610,981.43807700000002,11.151581,88.008873091627095]
[7620,289.63726500000001,7620,981.38944700000002,10.799113999999999,90.876848508127622]
[7630,296.356539,7630,981.34074799999996,10.409440999999999,94.274106361715297]
[7640,303.15216600000002,7640,981.29198199999996,10.008038000000001,98.050385300295616]
[7650,310.024765,7650,981.24316199999998,9.6101159999999997,102.10523598258335]
[7660,316.97495199999997,7660,981.19430299999999,9.2243250000000003,106.37030926382147]
[7670,324.00332500000002,7670,981.14541599999995,8.8552379999999999,110.79831123680695]
[7680,331.11044800000002,7680,981.09649999999999,8.5049329999999994,115.35617035431085]
[7690,338.29684099999997,7690,981.04754600000001,8.1739870000000003,{"$f":"D774/E774","v":120.02068831281478}]
[7700,345.56295699999998,7700,980.99853499999995,7.8620780000000003,124.77598606882302]
[7710,352.90916900000002,7710,980.94944799999996,7.568397,129.61125691477335]
[7720,360.33574800000002,7720,980.90027599999996,7.2920259999999999,134.51683743310844]
[7730,367.84284700000001,7730,980.85102500000005,7.0321129999999998,139.48169277143302]
[7740,375.43047300000001,7740,980.80172300000004,6.7875160000000001,144.50083403118313]
[7750,383.09846900000002,7750,980.75242600000001,6.5569940000000004,149.57348229996853]
[7760,390.84648399999998,7760,980.697405,6.3394190000000004,154.6983098924365]
[7770,398.673947,7770,980.67381,6.1338160000000004,159.8798871697488]
[7780,406.58003400000001,7780,980.62436600000001,5.9393029999999998,165.10765084724588]
[7790,414.56363900000002,7790,980.57498899999996,5.7550169999999996,170.38611510617605]
[7800,422.623335,7800,980.52559199999996,5.5802139999999998,175.7146933791428]
[7810,430.75733500000001,7810,980.47611300000005,5.4142239999999999,181.09263912981805]
[7820,438.96345000000002,7820,980.42650900000001,5.2563639999999996,186.52180651872666]
[7830,447.23904499999998,7830,980.37676099999999,5.1060140000000001,192.00432294153521]
[7840,455.58098799999999,7840,980.32688299999995,4.9626349999999997,197.54160501427165]
[7850,463.98559799999998,7850,980.27691500000003,4.8257459999999996,203.13479304546905]
[7860,472.44858699999997,7860,980.22691399999997,4.6949050000000003,208.78524996778421]
[7870,480.96500500000002,7870,980.17693099999997,4.5697020000000004,214.49471562915917]
[7880,489.52916900000002,7880,980.12699099999998,4.4497590000000002,220.26518537296064]
[7890,498.13459899999998,7890,980.07708700000001,4.3347300000000004,226.09876209129516]
[7900,506.77394700000002,7900,980.02717399999995,4.2243050000000002,231.99725730031329]
[7910,515.43892600000004,7910,979.97719700000005,4.1181970000000003,237.96268051285548]
[7920,524.120228,7920,979.92740800000001,4.01614,243.99732280249194]
[7930,532.80745100000001,7930,979.87714300000005,3.917875,250.10423839453787]
[7940,541.48901499999999,7940,979.82667300000003,3.8231809999999999,256.28571417361616]
[7950,550.15209100000004,7950,979.77608299999997,3.7318380000000002,262.54518095372839]
[7960,558.78251999999998,7960,979.72546299999999,3.6436480000000002,268.88587014991566]
[7970,567.36473699999999,7970,979.67490299999997,3.5584280000000001,275.3111494738688]
[7980,575.88171199999999,7980,979.62446199999999,3.4760219999999999,281.82343552486145]
[7990,584.31488300000001,7990,979.57414000000006,3.3962859999999999,288.42510318624522]
[8000,592.64411299999995,8000,979.523865,3.3190840000000001,295.11873306008522]
[8010,600.84765400000003,8010,979.47350400000005,3.2442850000000001,301.90735524160175]
[8020,608.90213300000005,8020,979.42289500000004,3.1717580000000001,308.79496323490002]
[8030,616.782557,8030,979.37189100000001,3.1013839999999999,315.78543353547963]
[8040,624.46234800000002,8040,979.32041200000003,3.0330629999999998,322.88165857418727]
[8050,631.91340400000001,8050,979.26848900000005,2.9667029999999999,330.08645927819538]
[8060,639.10619799999995,8060,979.21630000000005,2.9021949999999999,337.40541211048884]
[8070,646.00991999999997,8070,979.16433700000005,2.8394439999999999,344.84368665133036]
[8080,652.59265700000003,8080,982.79305899999997,2.7955909999999999,351.55108848182726]
[8090,658.82162400000004,8090,982.731447,2.7358609999999999,359.2037194141077]
[8100,664.66344800000002,8100,982.670703,2.6776140000000002,366.99490777983681]
[8110,670.08450000000005,8110,982.61061600000005,2.6209950000000002,374.89984376162488]
[8120,675.05128100000002,8120,982.551063,2.5667409999999999,382.80101615238937]
[8130,679.53086299999995,8130,982.49187800000004,2.5144959999999998,390.73113578228009]
[8140,683.49137099999996,8140,982.432861,2.462609,398.93984834782947]
[8150,686.90251499999999,8150,982.37381800000003,2.4112110000000002,407.41926691608489]
[8160,689.73614899999995,8160,982.31460100000004,2.3606989999999999,416.11175376445709]
[8170,691.96686199999999,8170,982.25513799999999,2.3112110000000001,424.99587359180964]
[8180,693.57257200000004,8180,982.19543699999997,2.262759,434.06983996086194]
[8190,694.53512599999999,8190,982.13556800000003,2.215322,443.33761322281816]
[8200,694.84087499999998,8200,982.07563200000004,2.1688909999999999,452.80082401559145]
[8210,694.48122000000001,8210,982.01572099999998,2.1234899999999999,462.45365930614224]
[8220,693.45310900000004,8220,981.95588999999995,2.0791210000000002,472.29376741421009]
[8230,691.75946399999998,8230,981.89614700000004,2.0357210000000001,482.33335854962445]
[8240,689.40953999999999,8240,981.83572600000002,1.993201,492.59243096907937]
[8250,686.41918999999996,8250,981.77856799999995,1.951487,503.09254840027114]
[8260,682.81103900000005,8260,981.71879100000001,1.9105529999999999,513.84012429909035]
[8270,678.61456699999997,8270,981.65885700000001,1.87035,524.85302590424249]
[8280,673.86608799999999,8280,981.59877300000005,1.8308549999999999,536.14227942682521]
[8290,668.60865100000001,8290,981.53856900000005,1.7920499999999999,547.71829413241824]
[8300,662.89185899999995,8300,981.478297,1.753922,559.59061862500153]
[8310,656.771612,8310,981.41801199999998,1.71645,571.77197821084212]
[8320,650.30981099999997,8320,981.35775000000001,1.6796150000000001,584.27541430625467]
[8330,643.57401500000003,8330,981.29751999999996,1.643394,{"$f":"D838/E838","v":597.11640665598145}]
[8340,636.63707099999999,8340,981.237301,1.607766,610.31101603093987]
[8350,629.57674299999996,8350,981.177055,1.572711,623.87625889308333]
[8360,622.47533099999998,8360,981.11673900000005,1.5382130000000001,637.82892161228642]
[8370,615.41930300000001,8370,981.05632800000001,1.5042500000000001,652.18968123649654]
[8380,608.49893099999997,8380,980.99582099999998,1.470801,666.98065951818091]
[8390,601.80793700000004,8390,980.93525799999998,1.4378489999999999,682.22411254589326]
[8400,595.44314099999997,8400,980.882205,1.4054180000000001,697.92916057713785]
[8410,589.50410099999999,8410,980.82034299999998,1.373416,714.1465826814308]
[8420,584.09273399999995,8420,980.75964199999999,1.341844,730.90436891322679]
[8430,579.31290799999999,8430,980.69896000000006,1.310684,748.23447909641084]
[8440,575.269991,8440,980.63828000000001,1.2799210000000001,766.17094336291063]
[8450,572.07035299999995,8450,980.57756800000004,1.249536,784.75335484531865]
[8460,569.82082200000002,8460,980.51678800000002,1.219543,804.00345703267533]
[8470,568.62810999999999,8470,980.45591400000001,1.189978,823.92776505111863]
[8480,568.59822499999996,8480,980.39494200000001,1.160839,844.55720560732368]
[8490,569.83591699999999,8490,980.33388600000001,1.1320889999999999,865.9512511825485]
[8500,572.44420100000002,8500,980.27277500000002,1.1036509999999999,888.209021692546]
[8510,576.52402099999995,8510,980.21164099999999,1.0753969999999999,911.48816762553736]
[8520,582.17412899999999,8520,980.15050599999995,1.047215,935.95919271591788]
[8530,589.49123199999997,8530,980.08937200000003,1.019155,961.66860977967042]
[8540,598.57048699999996,8540,980.02822200000003,0.99133199999999999,988.5973841256008]
[8550,609.50638300000003,8550,979.96702100000005,0.96387199999999995,1016.6982970767904]
[8560,622.39404999999999,8560,979.90494200000001,0.93684800000000001,1045.9593680084708]
[8570,637.33101899999997,8570,979.85429799999997,0.910273,1076.4400328253173]
[8580,654.41944599999999,8580,979.79293500000006,0.884104,1108.232668328613]
[8590,673.76879899999994,8590,979.73145399999999,0.85831500000000005,1141.4590843687922]
[8600,695.49902799999995,8600,979.66990299999998,0.83289000000000002,1176.2296377672922]
[8610,719.74423300000001,8610,979.60832100000005,0.80782100000000001,1212.6551810363931]
[8620,746.65687700000001,8620,979.54673600000001,0.78310000000000002,1250.8577908313114]
[8630,776.41263500000002,8630,979.48515899999995,0.75872300000000004,1290.9654234812967]
[8640,809.21599500000002,8640,979.42358300000001,0.73469099999999998,1333.1095426512643]
[8650,845.30681700000002,8650,979.36198400000001,0.71099900000000005,1377.4449528058408]
[8660,884.96809099999996,8660,979.30033400000002,0.68763099999999999,1424.1654811955832]
[8670,928.53528200000005,8670,979.238606,0.66456599999999999,1473.5009103685713]
[8680,976.40773300000001,8680,979.17679199999998,0.641795,1525.6846687805296]
[8690,1029.0627899999999,8690,979.11489700000004,0.61933800000000006,1580.9055749849031]
[8700,1087.073539,8700,979.05294700000002,0.59726000000000001,1639.240777885678]
[8710,1151.1313600000001,8710,978.99097700000004,0.57566200000000001,1700.6350549454369]
[8720,1222.0749639999999,8720,978.93017999999995,0.554678,1764.8621001734339]
[8730,1300.928177,8730,978.86787500000003,0.53444100000000005,1831.573316792686]
[8740,1388.9498229999999,8740,978.805882,0.51503399999999999,1900.4684778092321]
[8750,1487.6999149999999,8750,978.74385500000005,0.496309,1972.0453487645802]
[8760,1599.1290160000001,8760,978.68177300000002,0.477852,2048.0855432225876]
[8770,1725.6996389999999,8770,978.61960899999997,0.45927400000000002,2130.7968859547896]
[8780,1870.552848,8780,978.55735100000004,0.44053100000000001,2221.313258317803]
[8790,2037.7382439999999,8790,978.49499900000001,0.42181299999999999,2319.7364685298935]
[8800,2232.531536,8800,978.43257400000005,0.40332000000000001,2425.9460825151245]
[8810,2461.8680599999998,8810,978.37010599999996,0.38527499999999998,2539.4071922652652]
[8820,2734.9125130000002,8820,978.30762700000002,0.36837999999999999,2655.7023372604376]
[8830,3063.7311979999999,8830,978.24516000000006,0.354821,2757.0103235152374]
[8840,3463.8283590000001,8840,978.18271200000004,0.34715600000000002,2817.7036029911624]
[8850,3953.6418720000001,8850,978.120273,0.34269500000000003,2854.2005952815184]
[8860,4550.1247890000004,8860,978.057816,0.337368,2899.0829479974391]
[8870,5252.5954170000005,8870,977.99529199999995,0.33132600000000001,2951.7613830487189]
[8880,5999.8459140000004,8880,977.935744,0.32585500000000001,3001.1377575915667]
[8890,6601.8346959999999,8890,977.84298100000001,0.32216600000000001,3035.2147060831994]
[8900,6760.5717519999998,8900,977.78031799999997,0.31961800000000001,3059.2154321721555]
[8910,6344.3360570000004,8910,977.717534,0.31889400000000001,3065.9640319353766]
[8920,5576.0944909999998,8920,977.65466200000003,0.32004300000000002,3054.7603353299401]
[8930,4782.2376969999996,8930,977.59172100000001,0.32303300000000001,3026.2905678367224]
[8940,4191.8417289999998,8940,977.52872100000002,0.32783000000000001,2981.8159442393921]
[8950,3993.7813080000001,8950,977.46566900000005,0.33438699999999999,2923.1569080137688]
[8960,4302.9147970000004,8960,977.40256399999998,0.34261599999999998,2852.763922292012]
[8970,4731.1067480000002,8970,977.33940700000005,0.352404,{"$f":"D902/E902","v":2773.3493575555331}]
[8980,4632.3002699999997,8980,977.27619700000002,0.36363099999999998,2687.549183100451]
[8990,4154.5017150000003,8990,977.21293800000001,0.37617899999999999,2597.733892641535]
[9000,3652.6044219999999,9000,977.14963799999998,0.38994099999999998,2505.8909886367423]
[9010,3233.8850000000002,9010,977.08630600000004,0.40481200000000001,2413.6792041737895]
[9020,2898.514228,9020,977.02294800000004,0.42068899999999998,2322.4352146122196]
[9030,2628.140707,9030,976.959566,0.43747599999999998,2233.1729420585357]
[9040,2406.3625440000001,9040,976.89565500000003,0.45508999999999999,2146.5988156188887]
[9050,2221.1259650000002,9050,976.83299499999998,0.47346700000000003,2063.1490579068868]
[9060,2063.8691279999998,9060,976.76950599999998,0.492535,1983.1474027226491]
[9070,1928.472121,9070,976.70593699999995,0.512243,1906.7238341958796]
[9080,1810.4811239999999,9080,976.64228900000001,0.53254999999999997,1833.8978293118018]
[9090,1706.5874060000001,9090,976.57857100000001,0.55341899999999999,1764.6278335221596]
[9100,1614.2831619999999,9100,976.51479800000004,0.57481099999999996,1698.8450081852993]
[9110,1531.632249,9110,976.45099000000005,0.59669899999999998,1636.4213615239846]
[9120,1457.114857,9120,976.38716699999998,0.61906499999999998,1577.1965254052482]
[9130,1389.52017,9130,976.32334000000003,0.64190199999999997,1520.9850413302966]
[9140,1327.870721,9140,976.25950799999998,0.66520800000000002,1467.6003716130895]
[9150,1271.36806,9150,976.19565499999999,0.68898199999999998,1416.8667033391293]
[9160,1219.3530479999999,9160,976.131756,0.71320700000000004,1368.6513957378431]
[9170,1171.276357,9170,976.06777099999999,0.73789099999999996,1322.7804255642095]
[9180,1126.676234,9180,976.003648,0.76307199999999997,1279.0452906147782]
[9190,1085.161507,9190,975.93926599999998,0.78874500000000003,1237.3317941793607]
[9200,1046.3984419999999,9200,976.02209300000004,0.81424700000000005,1198.6806128852793]
[9210,1010.100454,9210,975.95292500000005,0.84029100000000001,1161.4463620341048]
[9220,976.01997800000004,9220,975.88847799999996,0.86517299999999997,1127.9691784186516]
[9230,943.94197899999995,9230,975.82388900000001,0.88605599999999995,1101.3117556903853]
[9240,913.67872799999998,9240,975.75922300000002,0.90031700000000003,1083.7951776985217]
[9250,885.065562,9250,975.69450900000004,0.91378199999999998,1067.7541350125084]
[9260,857.95741499999997,9260,975.62976600000002,0.93523800000000001,1043.1887562310342]
[9270,832.22596399999998,9270,975.56499799999995,0.96324900000000002,1012.7858923289823]
[9280,807.75725999999997,9280,975.50020500000005,0.993842,981.54455637817682]
[9290,784.44975899999997,9290,975.43538100000001,1.025234,951.42707030785175]
[9300,762.21266400000002,9300,975.37051899999994,1.0568169999999999,922.93227588125478]
[9310,740.96453299999996,9310,975.305612,1.0881479999999999,896.29867628300576]
[9320,720.63209400000005,9320,975.24065599999994,1.1185959999999999,871.8435038208612]
[9330,701.14924599999995,9330,975.17564700000003,1.1476569999999999,849.71001527459862]
[9340,682.45619099999999,9340,975.11058300000002,1.1755530000000001,829.49095702192926]
[9350,664.49870299999998,9350,975.04545900000005,1.2031149999999999,810.43413056939698]
[9360,647.22748999999999,9360,974.97983599999998,1.231071,791.97693390551797]
[9370,630.59764199999995,9370,974.91566899999998,1.2597309999999999,773.90781762138113]
[9380,614.56815900000004,9380,974.85043499999995,1.289121,756.21329184770082]
[9390,599.10153000000003,9390,974.78515300000004,1.3191649999999999,738.94103694382443]
[9400,584.16336999999999,9400,974.719829,1.3497669999999999,722.13932404629838]
[9410,569.72210800000005,9410,974.65446499999996,1.380835,705.84426452110495]
[9420,555.74870099999998,9420,974.58905900000002,1.4123110000000001,690.06688965815601]
[9430,542.21638900000005,9430,974.52361099999996,1.444167,674.79980570114117]
[9440,529.10047999999995,9440,974.45811900000001,1.4764010000000001,660.02266254222263]
[9450,516.37815499999999,9450,974.39258199999995,1.509026,645.70960473842069]
[9460,504.028299,9460,974.327001,1.5420560000000001,631.83632825267046]
[9470,492.03134599999998,9470,974.26137800000004,1.575499,618.38273334353119]
[9480,480.36914899999999,9480,974.19571800000006,1.609364,605.32963207826197]
[9490,469.02485100000001,9490,974.13002700000004,1.643667,592.65655817145444]
[9500,457.98278499999998,9500,974.06431299999997,1.6784239999999999,580.34460481975952]
[9510,447.22837299999998,9510,973.99859200000003,1.7136530000000001,568.37562330296737]
[9520,436.74804,9520,973.93942400000003,1.749323,556.7521972786044]
[9530,426.52913599999999,9530,973.87253699999997,1.785617,545.39833402123747]
[9540,416.55986799999999,9540,973.80665399999998,1.8225480000000001,534.31056630607259]
[9550,406.82923099999999,9550,973.74070800000004,1.860155,523.47288693684129]
[9560,397.32696099999998,9560,973.67470100000003,1.898417,512.88768537154908]
[9570,388.043476,9570,973.60863300000005,1.937271,502.56708173507997]
[9580,378.96983299999999,9580,973.542507,1.9765950000000001,492.53514604661041]
[9590,370.09768800000001,9590,973.47632999999996,2.0163509999999998,482.79110631035968]
[9600,361.41925600000002,9600,973.41011100000003,2.0566010000000001,473.31014183110869]
[9610,352.92728199999999,9610,973.34385799999995,2.0974300000000001,{"$f":"D966/E966","v":464.06500240770845}]
[9620,344.61500799999999,9620,973.27757199999996,2.138919,455.03245891966924]
[9630,336.47614900000002,9630,973.21125199999994,2.1811410000000002,446.19364451908422]
[9640,328.50486599999999,9640,973.14489000000003,2.2241279999999999,437.5399662249655]
[9650,320.69575099999997,9650,973.07847700000002,2.2678739999999999,429.07078479668627]
[9660,313.04380400000002,9660,973.01200500000004,2.3124020000000001,420.77978007284202]
[9670,305.54442,9670,972.94546400000002,2.3577439999999998,412.65950162528253]
[9680,298.193375,9680,972.87973499999998,2.40394,404.7021701872759]
[9690,290.98681599999998,9690,972.808764,2.4510190000000001,396.89972374755149]
[9700,283.92125099999998,9700,972.74203899999998,2.4990899999999998,389.23849841342252]
[9710,276.99354399999999,9710,972.67530199999999,2.5481880000000001,381.7125353388368]
[9720,270.20090800000003,9720,972.60854600000005,2.5983689999999999,374.31502069182631]
[9730,263.54090300000001,9730,972.54176900000004,2.6496930000000001,367.03941513224362]
[9740,257.011438,9740,972.474965,2.702232,359.87841347449074]
[9750,250.610769,9750,972.40812500000004,2.7560549999999999,352.82609563306977]
[9760,244.337502,9760,972.34123899999997,2.8112339999999998,345.87702019824746]
[9770,238.19060099999999,9770,972.27430100000004,2.867845,339.02609834213496]
[9780,232.16939300000001,9780,972.20730700000001,2.9259710000000001,332.26826479141454]
[9790,226.27357599999999,9790,972.14026100000001,2.9857,325.598774491744]
[9800,220.503232,9800,972.07317,3.047123,319.01343332710888]
[9810,214.858836,9810,972.00604099999998,3.1103299999999998,312.5089752534297]
[9820,209.341275,9820,971.93887600000005,3.175405,306.08343691592097]
[9830,203.95186000000001,9830,971.87167199999999,3.2424379999999999,299.73485136801384]
[9840,198.69234,9840,971.80301299999996,3.3115230000000002,293.46104888898549]
[9850,193.56492800000001,9850,971.73621700000001,3.3827690000000001,287.26058947566327]
[9860,188.57231100000001,9860,971.66891499999997,3.456305,281.12938962273296]
[9870,183.717671,9870,971.60154599999998,3.5323229999999999,275.06022127648009]
[9880,179.004704,9880,971.53411400000005,3.6110679999999999,269.04342814923456]
[9890,174.437634,9890,971.46662400000002,3.692771,263.07253387767616]
[9900,170.02122299999999,9900,971.39908700000001,3.7775940000000001,257.14756191374721]
[9910,165.760783,9910,971.33151099999998,3.8656929999999998,251.26969756780997]
[9920,161.66217399999999,9920,971.26390700000002,3.9572630000000002,245.43830091656784]
[9930,157.73180199999999,9930,971.19627600000001,4.0525390000000003,239.65130896951268]
[9940,153.976597,9940,971.12861599999997,4.1517119999999998,233.91040033605415]
[9950,150.403988,9950,971.06091900000001,4.2546439999999999,228.23552781384296]
[9960,147.021852,9960,970.99317199999996,4.360646,222.67186375596643]
[9970,143.83845700000001,9970,970.92536600000005,4.4702789999999997,217.19569762871626]
[9980,140.862369,9980,970.85749099999998,4.5852700000000004,211.73398534873627]
[9990,138.102352,9990,970.789535,4.7059920000000002,206.2879696778065]
[10000,135.56723500000001,10000,970.72495700000002,4.8325149999999999,200.87365626387088]
[null,null,10010,7.911543,1.9059E-2]
[null,null,10020,7.8920500000000002,1.9654999999999999E-2]
[null,null,10030,7.8726019999999997,2.0236000000000001E-2]
[null,null,10040,7.8531959999999996,2.0819000000000001E-2]
[null,null,10050,7.8338260000000002,2.1422E-2]
[null,null,10060,7.8144859999999996,2.2036E-2]
[null,null,10070,7.7951750000000004,2.2655999999999999E-2]
[null,null,10080,7.7758960000000004,2.3285E-2]
[null,null,10090,7.756653,2.3928000000000001E-2]
[null,null,10100,7.7374510000000001,2.4587000000000001E-2]
[null,null,10110,7.7182940000000002,2.5253999999999999E-2]
[null,null,10120,7.6991810000000003,2.5923000000000002E-2]
[null,null,10130,7.6801060000000003,2.6585000000000001E-2]
[null,null,10140,7.6610639999999997,2.7245999999999999E-2]
[null,null,10150,7.6420399999999997,2.7911999999999999E-2]
[null,null,10160,7.6229110000000002,2.8593E-2]
[null,null,10170,7.6036599999999996,2.9286E-2]
[null,null,10180,7.5847150000000001,3.0002999999999998E-2]
[null,null,10190,7.565823,3.0744E-2]
[null,null,10200,7.5469840000000001,3.1509000000000002E-2]
[null,null,10210,7.5282020000000003,3.2293000000000002E-2]
[null,null,10220,7.5094750000000001,3.3101999999999999E-2]
[null,null,10230,7.4907979999999998,3.3940999999999999E-2]
[null,null,10240,7.4721599999999997,3.4812000000000003E-2]
[null,null,10250,7.4535470000000004,3.5714999999999997E-2]
[null,null,10260,7.4349509999999999,3.6643000000000002E-2]
[null,null,10270,7.416366,3.7599E-2]
[null,null,10280,7.3977959999999996,3.8618E-2]
[null,null,10290,7.3792540000000004,3.9738000000000002E-2]
[null,null,10300,7.3607639999999996,4.0930000000000001E-2]
[null,null,10310,7.3423860000000003,4.2174000000000003E-2]
[null,null,10320,7.2972669999999997,4.3499999999999997E-2]
[null,null,10330,7.2834260000000004,4.4873000000000003E-2]
[null,null,10340,7.2650889999999997,4.6297999999999999E-2]
[null,null,10350,7.2468560000000002,4.7865999999999999E-2]
[null,null,10360,7.2287020000000002,4.9748000000000001E-2]
[null,null,10370,7.2106070000000004,5.1954E-2]
[null,null,10380,7.192558,5.4186999999999999E-2]
[null,null,10390,7.1745450000000002,5.6355000000000002E-2]
[null,null,10400,7.1565589999999997,5.8529999999999999E-2]
[null,null,10410,7.1385990000000001,6.0770999999999999E-2]
[null,null,10420,7.1206649999999998,6.3099000000000002E-2]
[null,null,10430,7.1027620000000002,6.5505999999999995E-2]
[null,null,10440,7.0848940000000002,6.7969000000000002E-2]
[null,null,10450,7.0670679999999999,7.0447999999999997E-2]
[null,null,10460,7.0492879999999998,7.2862999999999997E-2]
[null,null,10470,7.0315570000000003,7.5046000000000002E-2]
[null,null,10480,7.0145090000000003,7.6713000000000003E-2]
[null,null,10490,6.9954020000000003,7.7435000000000004E-2]
[null,null,10500,6.9777639999999996,7.6651999999999998E-2]
[null,null,10510,6.9601749999999996,7.3664999999999994E-2]
[null,null,10520,6.9426249999999996,6.7825999999999997E-2]
[null,null,10530,6.9251110000000002,5.8817000000000001E-2]
[null,null,10540,6.907635,4.6966000000000001E-2]
[null,null,10550,6.8901979999999998,3.3417000000000002E-2]
[null,null,10560,6.8728059999999997,2.0740999999999999E-2]
[null,null,10570,6.8554589999999997,1.6714E-2]
[null,null,10580,6.838158,2.6710000000000001E-2]
[null,null,10590,6.8208960000000003,4.1951000000000002E-2]
[null,null,10600,6.8036659999999998,5.8993999999999998E-2]
[null,null,10610,6.7864529999999998,7.7502000000000001E-2]
[null,null,10620,6.7692389999999998,9.7789000000000001E-2]
[null,null,10630,6.7519749999999998,0.120264]
[null,null,10640,6.7034039999999999,0.14518800000000001]
[null,null,10650,6.6884449999999998,0.17138500000000001]
[null,null,10660,6.671449,0.196327]
[null,null,10670,6.6544879999999997,0.21516099999999999]
[null,null,10680,6.6375710000000003,0.222885]
[null,null,10690,6.6207079999999996,0.21818599999999999]
[null,null,10700,6.6039000000000003,0.20449300000000001]
[null,null,10710,6.5871449999999996,0.186862]
[null,null,10720,6.5704349999999998,0.16892499999999999]
[null,null,10730,6.5537619999999999,0.15243200000000001]
[null,null,10740,6.5371180000000004,0.137934]
[null,null,10750,6.5205039999999999,0.12542]
[null,null,10760,6.5039199999999999,0.11465599999999999]
[null,null,10770,6.4873750000000001,0.105367]
[null,null,10780,6.4708779999999999,9.7316E-2]
[null,null,10790,6.4544420000000002,9.0296000000000001E-2]
[null,null,10800,6.4381199999999996,8.4132999999999999E-2]
[null,null,10810,6.4208049999999997,7.8671000000000005E-2]
[null,null,10820,6.4044889999999999,7.3832999999999996E-2]
[null,null,10830,6.3882139999999996,6.9504999999999997E-2]
[null,null,10840,6.3719700000000001,6.5605999999999998E-2]
[null,null,10850,6.3557540000000001,6.2072000000000002E-2]
[null,null,10860,6.3395650000000003,5.8858000000000001E-2]
[null,null,10870,6.3234069999999996,5.5921999999999999E-2]
[null,null,10880,6.3072869999999996,5.3231000000000001E-2]
[null,null,10890,6.291207,5.0756999999999997E-2]
[null,null,10900,6.2751720000000004,4.8478E-2]
[null,null,10910,6.2591789999999996,4.6373999999999999E-2]
[null,null,10920,6.2432239999999997,4.4430999999999998E-2]
[null,null,10930,6.2273009999999998,4.2633999999999998E-2]
[null,null,10940,6.2114060000000002,4.0962999999999999E-2]
[null,null,10950,6.1955340000000003,3.9402E-2]
[null,null,10960,6.1790950000000002,3.7939000000000001E-2]
[null,null,10970,6.1634830000000003,3.6569999999999998E-2]
[null,null,10980,6.1477240000000002,3.5285999999999998E-2]
[null,null,10990,6.1320269999999999,3.4095E-2]
[null,null,11000,6.1163869999999996,3.3015999999999997E-2]
[null,null,11010,6.1007949999999997,3.2063000000000001E-2]
[null,null,11020,6.0852449999999996,3.1234999999999999E-2]
[null,null,11030,6.0697260000000002,3.056E-2]
[null,null,11040,6.0542350000000003,3.0099000000000001E-2]
[null,null,11050,6.0387740000000001,2.9933000000000001E-2]
[null,null,11060,6.0233489999999996,3.0136E-2]
[null,null,11070,6.0079750000000001,3.0578999999999999E-2]
[null,null,11080,5.9926630000000003,3.0440999999999999E-2]
[null,null,11090,5.9774209999999997,2.9551999999999998E-2]
[null,null,11100,5.9622450000000002,2.8726999999999999E-2]
[null,null,11110,5.9471220000000002,2.7833E-2]
[null,null,11120,5.9295850000000003,2.6793000000000001E-2]
[null,null,11130,6.004721,2.5092E-2]
[null,null,11140,5.9900219999999997,2.4022999999999999E-2]
[null,null,11150,5.9752070000000002,2.3002000000000002E-2]
[null,null,11160,5.9603440000000001,2.2030999999999999E-2]
[null,null,11170,5.9454589999999996,2.1118999999999999E-2]
[null,null,11180,5.9305779999999997,2.0277E-2]
[null,null,11190,5.9157279999999997,1.9507E-2]
[null,null,11200,5.9009320000000001,1.8828000000000001E-2]
[null,null,11210,5.8862019999999999,1.8266999999999999E-2]
[null,null,11220,5.8715400000000004,1.7846999999999998E-2]
[null,null,11230,5.8569370000000003,1.7564E-2]
[null,null,11240,5.8423800000000004,1.7378999999999999E-2]
[null,null,11250,5.8278530000000002,1.7231E-2]
[null,null,11260,5.8133480000000004,1.7069999999999998E-2]
[null,null,11270,5.7988679999999997,1.6872999999999999E-2]
[null,null,11280,5.7854219999999996,1.6641E-2]
[null,null,11290,5.7703309999999997,1.6372999999999999E-2]
[null,null,11300,5.755935,1.6084999999999999E-2]
[null,null,11310,5.7416090000000004,1.5793999999999999E-2]
[null,null,11320,5.7273500000000004,1.5509999999999999E-2]
[null,null,11330,5.7131499999999997,1.523E-2]
[null,null,11340,5.698995,1.4945E-2]
[null,null,11350,5.6848700000000001,1.4657E-2]
[null,null,11360,5.6707619999999999,1.4364999999999999E-2]
[null,null,11370,5.6566660000000004,1.4064E-2]
[null,null,11380,5.6425879999999999,1.3733E-2]
[null,null,11390,5.628539,1.3337999999999999E-2]
[null,null,11400,5.6145389999999997,1.2888E-2]
[null,null,11410,5.6006099999999996,1.2496999999999999E-2]
[null,null,11420,5.5867719999999998,1.2194E-2]
[null,null,11430,5.5730639999999996,1.1927999999999999E-2]
[null,null,11440,5.5478269999999998,1.1624000000000001E-2]
[null,null,11450,5.5488660000000003,1.1344E-2]
[null,null,11460,5.5351489999999997,1.1083000000000001E-2]
[null,null,11470,5.5215319999999997,1.082E-2]
[null,null,11480,5.5079690000000001,1.0605E-2]
[null,null,11490,5.4944410000000001,1.0505E-2]
[null,null,11500,5.480944,1.0454E-2]
[null,null,11510,5.4674769999999997,1.038E-2]
[null,null,11520,5.4540430000000004,1.0281E-2]
[null,null,11530,5.4406470000000002,1.0168999999999999E-2]
[null,null,11540,5.4272910000000003,1.0052E-2]
[null,null,11550,5.4139790000000003,9.9310000000000006E-3]
[null,null,11560,5.4007129999999997,9.8029999999999992E-3]
[null,null,11570,5.3874950000000004,9.6699999999999998E-3]
[null,null,11580,5.3743270000000001,9.5420000000000001E-3]
[null,null,11590,5.3612149999999996,9.4210000000000006E-3]
[null,null,11600,5.3485170000000002,9.299E-3]
[null,null,11610,5.3352919999999999,9.1540000000000007E-3]
[null,null,11620,5.3222849999999999,8.9789999999999991E-3]
[null,null,11630,5.3093130000000004,8.7519999999999994E-3]
[null,null,11640,5.2963779999999998,8.4639999999999993E-3]
[null,null,11650,5.2834849999999998,8.1250000000000003E-3]
[null,null,11660,5.2706359999999997,7.7780000000000002E-3]
[null,null,11670,5.2578339999999999,7.4749999999999999E-3]
[null,null,11680,5.2450799999999997,7.2610000000000001E-3]
[null,null,11690,5.232367,7.156E-3]
[null,null,11700,5.2196889999999998,7.1599999999999997E-3]
[null,null,11710,5.2070309999999997,7.2680000000000002E-3]
[null,null,11720,5.1943840000000003,7.4809999999999998E-3]
[null,null,11730,5.181737,7.7970000000000001E-3]
[null,null,11740,5.1690909999999999,8.2019999999999992E-3]
[null,null,11750,5.1564540000000001,8.6920000000000001E-3]
[null,null,11760,5.1491579999999999,9.9439999999999997E-3]
[null,null,11770,5.1370519999999997,1.0500000000000001E-2]
[null,null,11780,5.1243239999999997,1.0954E-2]
[null,null,11790,5.1117010000000001,1.1514999999999999E-2]
[null,null,11800,5.0991809999999997,1.2683E-2]
[null,null,11810,5.0867560000000003,1.3166000000000001E-2]
[null,null,11820,5.074408,1.2418999999999999E-2]
[null,null,11830,5.0621150000000004,1.1521999999999999E-2]
[null,null,11840,5.0498529999999997,1.0815E-2]
[null,null,11850,5.0376079999999996,1.0318000000000001E-2]
[null,null,11860,5.0253750000000004,9.9909999999999999E-3]
[null,null,11870,5.0131610000000002,9.7929999999999996E-3]
[null,null,11880,5.0009819999999996,9.6950000000000005E-3]
[null,null,11890,4.9888539999999999,9.6989999999999993E-3]
[null,null,11900,4.9767929999999998,9.7940000000000006E-3]
[null,null,11910,4.9648070000000004,9.9550000000000003E-3]
[null,null,11920,4.9521319999999998,1.0160000000000001E-2]
[null,null,11930,4.9432340000000003,1.0401000000000001E-2]
[null,null,11940,4.9314340000000003,1.0683E-2]
[null,null,11950,4.9196350000000004,1.0999999999999999E-2]
[null,null,11960,4.9078439999999999,1.1358E-2]
[null,null,11970,4.8960679999999996,1.1766E-2]
[null,null,11980,4.8843189999999996,1.2226000000000001E-2]
[null,null,11990,4.8726130000000003,1.2741000000000001E-2]
[null,null,12000,4.8609650000000002,1.3311E-2]
[null,null,12010,4.84938,1.3939E-2]
[null,null,12020,4.8378560000000004,1.4629E-2]
[null,null,12030,4.8263860000000003,1.5387E-2]
[null,null,12040,4.8149559999999996,1.6219999999999998E-2]
[null,null,12050,4.8035569999999996,1.7132000000000001E-2]
[null,null,12060,4.7921870000000002,1.8137E-2]
[null,null,12070,4.7808669999999998,1.9255000000000001E-2]
[null,null,12080,4.7741939999999996,2.0531000000000001E-2]
[null,null,12090,4.7620630000000004,2.1944000000000002E-2]
[null,null,12100,4.7508319999999999,2.3543999999999999E-2]
[null,null,12110,4.7396760000000002,2.537E-2]
[null,null,12120,4.7285899999999996,2.7466000000000001E-2]
[null,null,12130,4.7175580000000004,2.9878999999999999E-2]
[null,null,12140,4.7065640000000002,3.2681000000000002E-2]
[null,null,12150,4.6955939999999998,3.5934000000000001E-2]
[null,null,12160,4.6846410000000001,3.9633000000000002E-2]
[null,null,12170,4.6737120000000001,4.3636000000000001E-2]
[null,null,12180,4.6628179999999997,4.7524999999999998E-2]
[null,null,12190,4.6519769999999996,5.0442000000000001E-2]
[null,null,12200,4.6412000000000004,5.1223999999999999E-2]
[null,null,12210,4.6304930000000004,4.9175000000000003E-2]
[null,null,12220,4.6198430000000004,4.4653999999999999E-2]
[null,null,12230,4.609229,3.8799E-2]
[null,null,12240,4.5971650000000004,3.2714E-2]
[null,null,12250,4.6134579999999996,2.6873000000000001E-2]
[null,null,12260,4.6030990000000003,2.1767999999999999E-2]
[null,null,12270,4.5926850000000004,1.7236999999999999E-2]
[null,null,12280,4.5822729999999998,1.3206000000000001E-2]
[null,null,12290,4.571898,9.6600000000000002E-3]
[null,null,12300,4.5615880000000004,6.7990000000000004E-3]
[null,null,12310,4.5513620000000001,5.3629999999999997E-3]
[null,null,12320,4.5412229999999996,6.1729999999999997E-3]
[null,null,12330,4.5311589999999997,8.3879999999999996E-3]
[null,null,12340,4.521147,1.0862999999999999E-2]
[null,null,12350,4.511164,1.3024000000000001E-2]
[null,null,12360,4.5011929999999998,1.4599000000000001E-2]
[null,null,12370,4.4912320000000001,1.5517E-2]
[null,null,12380,4.4812960000000004,1.5854E-2]
[null,null,12390,4.4714159999999996,1.5755999999999999E-2]
[null,null,12400,4.4628909999999999,1.5379E-2]
[null,null,12410,4.4527279999999996,1.4836E-2]
[null,null,12420,4.4430670000000001,1.4229E-2]
[null,null,12430,4.4334769999999999,1.3625999999999999E-2]
[null,null,12440,4.4239369999999996,1.3056E-2]
[null,null,12450,4.4144189999999996,1.2512000000000001E-2]
[null,null,12460,4.404903,1.1982E-2]
[null,null,12470,4.3953800000000003,1.1462999999999999E-2]
[null,null,12480,4.3858629999999996,1.0951000000000001E-2]
[null,null,12490,4.376379,1.0423E-2]
[null,null,12500,4.3669609999999999,9.8160000000000001E-3]
[null,null,12510,4.3576370000000004,9.0320000000000001E-3]
[null,null,12520,4.3484230000000004,8.1180000000000002E-3]
[null,null,12530,4.3393139999999999,7.4180000000000001E-3]
[null,null,12540,4.3302889999999996,7.0150000000000004E-3]
[null,null,12550,4.3213090000000003,6.7320000000000001E-3]
[null,null,12560,4.3140460000000003,6.4469999999999996E-3]
[null,null,12570,4.3102210000000003,6.1069999999999996E-3]
[null,null,12580,4.3013269999999997,5.849E-3]
[null,null,12590,4.2924620000000004,5.5900000000000004E-3]
[null,null,12600,4.2836379999999998,5.3480000000000003E-3]
[null,null,12610,4.2748759999999999,5.1599999999999997E-3]
[null,null,12620,4.2661850000000001,5.012E-3]
[null,null,12630,4.2575609999999999,4.8719999999999996E-3]
[null,null,12640,4.2489869999999996,4.7359999999999998E-3]
[null,null,12650,4.240437,4.6080000000000001E-3]
[null,null,12660,4.2318920000000002,4.4939999999999997E-3]
[null,null,12670,4.2233470000000004,4.3959999999999997E-3]
[null,null,12680,4.2148159999999999,4.3099999999999996E-3]
[null,null,12690,4.2063290000000002,4.2339999999999999E-3]
[null,null,12700,4.1979249999999997,4.1679999999999998E-3]
[null,null,12710,4.1896360000000001,4.1190000000000003E-3]
[null,null,12720,4.1812100000000001,4.0920000000000002E-3]
[null,null,12730,4.1739009999999999,4.0810000000000004E-3]
[null,null,12740,4.1659079999999999,4.0899999999999999E-3]
[null,null,12750,4.1579050000000004,4.1159999999999999E-3]
[null,null,12760,4.1498549999999996,4.1580000000000002E-3]
[null,null,12770,4.1417390000000003,4.2059999999999997E-3]
[null,null,12780,4.1335790000000001,4.2550000000000001E-3]
[null,null,12790,4.1254350000000004,4.3059999999999999E-3]
[null,null,12800,4.1173929999999999,4.3629999999999997E-3]
[null,null,12810,4.1095420000000003,4.4289999999999998E-3]
[null,null,12820,4.1019399999999999,4.5059999999999996E-3]
[null,null,12830,4.0945840000000002,4.5880000000000001E-3]
[null,null,12840,4.0873980000000003,4.6670000000000001E-3]
[null,null,12850,4.0802100000000001,4.7540000000000004E-3]
[null,null,12860,4.0727159999999998,4.8630000000000001E-3]
[null,null,12870,4.0641379999999998,4.986E-3]
[null,null,12880,11.839553,3.5069000000000003E-2]
[null,null,12890,11.814747000000001,3.4175999999999998E-2]
[null,null,12900,11.792021999999999,3.3666000000000001E-2]
[null,null,12910,11.768756,3.3876000000000003E-2]
[null,null,12920,11.745277,3.4602000000000001E-2]
[null,null,12930,11.7218,3.4269000000000001E-2]
[null,null,12940,11.698468999999999,3.2554E-2]
[null,null,12950,11.675354,3.0464999999999999E-2]
[null,null,12960,11.652459,2.8504000000000002E-2]
[null,null,12970,11.629732000000001,2.6761E-2]
[null,null,12980,11.607094,2.5231E-2]
[null,null,12990,11.584467999999999,2.3935000000000001E-2]
[null,null,13000,11.561799000000001,2.2924E-2]
[null,null,13010,11.539072000000001,2.2204999999999999E-2]
[null,null,13020,11.516306,2.1658E-2]
[null,null,13030,11.493542,2.1128000000000001E-2]
[null,null,13040,11.470307999999999,2.0535999999999999E-2]
[null,null,13050,11.449384,1.9883999999999999E-2]
[null,null,13060,11.426933,1.9186999999999999E-2]
[null,null,13070,11.404574999999999,1.8473E-2]
[null,null,13080,11.382286000000001,1.7766000000000001E-2]
[null,null,13090,11.360028,1.7082E-2]
[null,null,13100,11.337774,1.6428000000000002E-2]
[null,null,13110,11.315511000000001,1.5799000000000001E-2]
[null,null,13120,11.293248,1.5192000000000001E-2]
[null,null,13130,11.271011,1.4600999999999999E-2]
[null,null,13140,11.248832,1.4022E-2]
[null,null,13150,11.226736000000001,1.3454000000000001E-2]
[null,null,13160,11.204737,1.2892000000000001E-2]
[null,null,13170,11.182834,1.2326999999999999E-2]
[null,null,13180,11.161011,1.1757E-2]
[null,null,13190,11.13926,1.1183E-2]
[null,null,13200,11.123154,1.0611000000000001E-2]
[null,null,13210,11.100363,1.0002E-2]
[null,null,13220,11.078619,9.3740000000000004E-3]
[null,null,13230,11.056891,8.7430000000000008E-3]
[null,null,13240,11.035204999999999,8.1359999999999991E-3]
[null,null,13250,11.013579999999999,7.5929999999999999E-3]
[null,null,13260,10.992025,7.1650000000000004E-3]
[null,null,13270,10.97054,6.829E-3]
[null,null,13280,10.949115000000001,6.5370000000000003E-3]
[null,null,13290,10.927735999999999,6.2639999999999996E-3]
[null,null,13300,10.906388,6.0350000000000004E-3]
[null,null,13310,10.885061,5.9680000000000002E-3]
[null,null,13320,10.863757,6.254E-3]
[null,null,13330,10.842479000000001,6.9249999999999997E-3]
[null,null,13340,10.82124,7.8600000000000007E-3]
[null,null,13350,10.800041999999999,8.9169999999999996E-3]
[null,null,13360,10.779717,1.0000999999999999E-2]
[null,null,13370,10.754495,1.1087E-2]
[null,null,13380,10.733458000000001,1.2173E-2]
[null,null,13390,10.712486,1.3292999999999999E-2]
[null,null,13400,10.691565000000001,1.4463E-2]
[null,null,13410,10.670688,1.5692999999999999E-2]
[null,null,13420,10.649857000000001,1.7002E-2]
[null,null,13430,10.629077000000001,1.8405999999999999E-2]
[null,null,13440,10.608352999999999,1.9916E-2]
[null,null,13450,10.587688999999999,2.1552000000000002E-2]
[null,null,13460,10.567083999999999,2.334E-2]
[null,null,13470,10.546533999999999,2.5308000000000001E-2]
[null,null,13480,10.526032000000001,2.7474999999999999E-2]
[null,null,13490,10.505572000000001,2.9825000000000001E-2]
[null,null,13500,10.485149,3.2273999999999997E-2]
[null,null,13510,10.464764000000001,3.4624000000000002E-2]
[null,null,13520,10.443688999999999,3.6469000000000001E-2]
[null,null,13530,10.423771,3.7111999999999999E-2]
[null,null,13540,10.403558,3.5458999999999997E-2]
[null,null,13550,10.383387000000001,3.0353999999999999E-2]
[null,null,13560,10.363261,2.1347999999999999E-2]
[null,null,13570,10.343173999999999,9.3340000000000003E-3]
[null,null,13580,10.323123000000001,6.7229999999999998E-3]
[null,null,13590,10.303106,2.2405999999999999E-2]
[null,null,13600,10.28313,4.0946000000000003E-2]
[null,null,13610,10.263207,6.3145999999999994E-2]
[null,null,13620,10.24335,8.9658000000000002E-2]
[null,null,13630,10.223571,0.116536]
[null,null,13640,10.20387,0.131023]
[null,null,13650,10.184232,0.125365]
[null,null,13660,10.164622,0.10946599999999999]
[null,null,13670,10.144966,9.3382999999999994E-2]
[null,null,13680,10.130051,8.0155000000000004E-2]
[null,null,13690,9.9248469999999998,7.0251999999999995E-2]
[null,null,13700,9.9053989999999992,6.2106000000000001E-2]
[null,null,13710,9.8857520000000001,5.5585000000000002E-2]
[null,null,13720,9.8660409999999992,5.0261E-2]
[null,null,13730,9.8463250000000002,4.5814000000000001E-2]
[null,null,13740,9.8266500000000008,4.2039E-2]
[null,null,13750,9.807048,3.8802000000000003E-2]
[null,null,13760,9.7875370000000004,3.5999000000000003E-2]
[null,null,13770,9.7681179999999994,3.3543000000000003E-2]
[null,null,13780,9.7487770000000005,3.1368E-2]
[null,null,13790,9.7294940000000008,2.9423999999999999E-2]
[null,null,13800,9.710248,2.7675999999999999E-2]
[null,null,13810,9.6910249999999998,2.6100000000000002E-2]
[null,null,13820,9.671818,2.4673E-2]
[null,null,13830,9.6526270000000007,2.3373999999999999E-2]
[null,null,13840,9.6326490000000007,2.2183000000000001E-2]
[null,null,13850,9.6141939999999995,2.1099E-2]
[null,null,13860,9.595186,2.0105000000000001E-2]
[null,null,13870,9.5762420000000006,1.9196000000000001E-2]
[null,null,13880,9.5573589999999999,1.8366E-2]
[null,null,13890,9.538532,1.7617000000000001E-2]
[null,null,13900,9.5197529999999997,1.6943E-2]
[null,null,13910,9.5010180000000002,1.6336E-2]
[null,null,13920,9.4823280000000008,1.5792E-2]
[null,null,13930,9.4636849999999999,1.5316E-2]
[null,null,13940,9.445093,1.4917E-2]
[null,null,13950,9.4265500000000007,1.4607E-2]
[null,null,13960,9.4080480000000009,1.4378E-2]
[null,null,13970,9.3895689999999998,1.4213999999999999E-2]
[null,null,13980,9.3710889999999996,1.4149999999999999E-2]
[null,null,13990,9.3525539999999996,1.4234999999999999E-2]
[null,null,14000,9.3789169999999995,1.4504E-2]
[null,null,14010,9.3564410000000002,1.5001E-2]
[null,null,14020,9.338165,1.5720000000000001E-2]
[null,null,14030,9.319896,1.6296000000000001E-2]
[null,null,14040,9.3016889999999997,1.5715E-2]
[null,null,14050,9.2835739999999998,1.3259E-2]
[null,null,14060,9.2655650000000005,1.0147E-2]
[null,null,14070,9.2476559999999992,7.7299999999999999E-3]
[null,null,14080,9.2298299999999998,6.3220000000000004E-3]
[null,null,14090,9.2120599999999992,5.7999999999999996E-3]
[null,null,14100,9.1943190000000001,5.9389999999999998E-3]
[null,null,14110,9.1765899999999991,6.4530000000000004E-3]
[null,null,14120,9.1588689999999993,7.0280000000000004E-3]
[null,null,14130,9.1411660000000001,7.3819999999999997E-3]
[null,null,14140,9.1235009999999992,7.391E-3]
[null,null,14150,9.1058880000000002,7.1320000000000003E-3]
[null,null,14160,9.0884999999999998,6.7679999999999997E-3]
[null,null,14170,9.0703029999999991,6.437E-3]
[null,null,14180,9.0529340000000005,6.1960000000000001E-3]
[null,null,14190,9.0356380000000005,6.0720000000000001E-3]
[null,null,14200,9.0183859999999996,6.0369999999999998E-3]
[null,null,14210,9.0011609999999997,6.0309999999999999E-3]
[null,null,14220,8.9839559999999992,5.9950000000000003E-3]
[null,null,14230,8.9667779999999997,5.8929999999999998E-3]
[null,null,14240,8.9496439999999993,5.7210000000000004E-3]
[null,null,14250,8.9325749999999999,5.4990000000000004E-3]
[null,null,14260,8.9155899999999999,5.2509999999999996E-3]
[null,null,14270,8.8986959999999993,4.9969999999999997E-3]
[null,null,14280,8.8818870000000008,4.751E-3]
[null,null,14290,8.8651459999999993,4.542E-3]
[null,null,14300,8.8484449999999999,4.4039999999999999E-3]
[null,null,14310,8.8317510000000006,4.3870000000000003E-3]
[null,null,14320,8.8072210000000002,4.509E-3]
[null,null,14330,8.7910520000000005,4.9849999999999998E-3]
[null,null,14340,8.7745130000000007,5.7780000000000001E-3]
[null,null,14350,8.758006,6.7840000000000001E-3]
[null,null,14360,8.7415590000000005,7.8120000000000004E-3]
[null,null,14370,8.725187,8.6870000000000003E-3]
[null,null,14380,8.7088929999999998,9.2820000000000003E-3]
[null,null,14390,8.6926670000000001,9.6360000000000005E-3]
[null,null,14400,8.6764939999999999,9.8600000000000007E-3]
[null,null,14410,8.6603539999999999,1.0038E-2]
[null,null,14420,8.6442370000000004,1.0229E-2]
[null,null,14430,8.6281420000000004,1.0459E-2]
[null,null,14440,8.6120789999999996,1.0710000000000001E-2]
[null,null,14450,8.5960680000000007,1.0947999999999999E-2]
[null,null,14460,8.5801289999999995,1.1172E-2]
[null,null,14470,8.564273,1.1379999999999999E-2]
[null,null,14480,8.5497160000000001,1.1571E-2]
[null,null,14490,8.5266470000000005,1.1726E-2]
[null,null,14500,8.5109309999999994,1.1917000000000001E-2]
[null,null,14510,8.4952869999999994,1.2114E-2]
[null,null,14520,8.4796800000000001,1.2314E-2]
[null,null,14530,8.4641009999999994,1.2522999999999999E-2]
[null,null,14540,8.4485600000000005,1.2747E-2]
[null,null,14550,8.4330750000000005,1.2985999999999999E-2]
[null,null,14560,8.4176649999999995,1.3240999999999999E-2]
[null,null,14570,8.4023439999999994,1.3514E-2]
[null,null,14580,8.3871129999999994,1.3807E-2]
[null,null,14590,8.3719579999999993,1.4121999999999999E-2]
[null,null,14600,8.3568529999999992,1.4458E-2]
[null,null,14610,8.3417720000000006,1.4808E-2]
[null,null,14620,8.3266910000000003,1.5162999999999999E-2]
[null,null,14630,8.3115939999999995,1.5514E-2]
[null,null,14640,8.2938019999999995,1.5866999999999999E-2]
[null,null,14650,8.2795850000000009,1.6215E-2]
[null,null,14660,8.2646800000000002,1.6582E-2]
[null,null,14670,8.2498830000000005,1.7016E-2]
[null,null,14680,8.2352019999999992,1.7566999999999999E-2]
[null,null,14690,8.2206229999999998,1.8242999999999999E-2]
[null,null,14700,8.2061089999999997,1.9012000000000001E-2]
[null,null,14710,8.1916139999999995,1.9864E-2]
[null,null,14720,8.1770949999999996,2.0815E-2]
[null,null,14730,8.1625320000000006,2.188E-2]
[null,null,14740,8.1479379999999999,2.3002000000000002E-2]
[null,null,14750,8.1333660000000005,2.3751999999999999E-2]
[null,null,14760,8.1188990000000008,2.3019999999999999E-2]
[null,null,14770,8.1046379999999996,2.1794000000000001E-2]
[null,null,14780,8.0906889999999994,2.1686E-2]
[null,null,14790,8.0771660000000001,2.2015E-2]
[null,null,14800,8.0654310000000002,2.2377999999999999E-2]
[null,null,14810,6.7605300000000002,1.3795999999999999E-2]
[null,null,14820,6.7422870000000001,1.4149999999999999E-2]
[null,null,14830,6.724234,1.4532E-2]
[null,null,14840,6.7061400000000004,1.4943E-2]
[null,null,14850,6.6879220000000004,1.5391999999999999E-2]
[null,null,14860,6.6695609999999999,1.5866999999999999E-2]
[null,null,14870,6.6510870000000004,1.6358000000000001E-2]
[null,null,14880,6.6325599999999998,1.6867E-2]
[null,null,14890,6.6140489999999996,1.7396999999999999E-2]
[null,null,14900,6.5956130000000002,1.7944999999999999E-2]
[null,null,14910,6.5772849999999998,1.8502999999999999E-2]
[null,null,14920,6.559069,1.9056E-2]
[null,null,14930,6.5409420000000003,1.9595000000000001E-2]
[null,null,14940,6.5228659999999996,2.0122000000000001E-2]
[null,null,14950,6.5047980000000001,2.0646000000000001E-2]
[null,null,14960,6.4866429999999999,2.1177000000000001E-2]
[null,null,14970,6.4682500000000003,2.1711999999999999E-2]
[null,null,14980,6.4501489999999997,2.2265E-2]
[null,null,14990,6.4320839999999997,2.2837E-2]
[null,null,15000,6.4140779999999999,2.3425999999999999E-2]
[null,null,15010,6.3961490000000003,2.4027E-2]
[null,null,15020,6.3783050000000001,2.4643999999999999E-2]
[null,null,15030,6.3605349999999996,2.528E-2]
[null,null,15040,6.3428180000000003,2.5937999999999999E-2]
[null,null,15050,6.325126,2.6613000000000001E-2]
[null,null,15060,6.307436,2.7300999999999999E-2]
[null,null,15070,6.2897369999999997,2.8003E-2]
[null,null,15080,6.2720349999999998,2.8759E-2]
[null,null,15090,6.2543490000000004,2.9610999999999998E-2]
[null,null,15100,6.2367150000000002,3.0528E-2]
[null,null,15110,6.2192030000000003,3.1482999999999997E-2]
[null,null,15120,6.1789820000000004,3.2496999999999998E-2]
[null,null,15130,6.1673020000000003,3.3552999999999999E-2]
[null,null,15140,6.1498590000000002,3.4638000000000002E-2]
[null,null,15150,6.1325260000000004,3.5825000000000003E-2]
[null,null,15160,6.1152620000000004,3.7239000000000001E-2]
[null,null,15170,6.0980439999999998,3.8887999999999999E-2]
[null,null,15180,6.0808549999999997,4.0556000000000002E-2]
[null,null,15190,6.0636890000000001,4.2179000000000001E-2]
[null,null,15200,6.0465460000000002,4.3809000000000001E-2]
[null,null,15210,6.0294309999999998,4.5488000000000001E-2]
[null,null,15220,6.0123540000000002,4.7230000000000001E-2]
[null,null,15230,5.9953200000000004,4.9026E-2]
[null,null,15240,5.9783330000000001,5.0856999999999999E-2]
[null,null,15250,5.9613930000000002,5.2690000000000001E-2]
[null,null,15260,5.9444970000000001,5.4466000000000001E-2]
[null,null,15270,5.9276429999999998,5.6057000000000003E-2]
[null,null,15280,5.9114599999999999,5.7251000000000003E-2]
[null,null,15290,5.8933200000000001,5.7726E-2]
[null,null,15300,5.8765309999999999,5.7063000000000003E-2]
[null,null,15310,5.859788,5.4739999999999997E-2]
[null,null,15320,5.843089,5.0269000000000001E-2]
[null,null,15330,5.8264339999999999,4.3413E-2]
[null,null,15340,5.8098270000000003,3.4412999999999999E-2]
[null,null,15350,5.793266,2.4114E-2]
[null,null,15360,5.7767489999999997,1.4446000000000001E-2]
[null,null,15370,5.7602739999999999,1.1780000000000001E-2]
[null,null,15380,5.7438349999999998,1.9945000000000001E-2]
[null,null,15390,5.7274240000000001,3.1622999999999998E-2]
[null,null,15400,5.7110349999999999,4.4483000000000002E-2]
[null,null,15410,5.6946560000000002,5.8363999999999999E-2]
[null,null,15420,5.678274,7.3527999999999996E-2]
[null,null,15430,5.6618399999999998,9.0287999999999993E-2]
[null,null,15440,5.6070060000000002,0.108933]
[null,null,15450,5.5930260000000001,0.12839900000000001]
[null,null,15460,5.5769060000000001,0.14688000000000001]
[null,null,15470,5.5608170000000001,0.16076799999999999]
[null,null,15480,5.5447680000000004,0.16637199999999999]
[null,null,15490,5.5287649999999999,0.162718]
[null,null,15500,5.5128130000000004,0.15232899999999999]
[null,null,15510,5.4969109999999999,0.13900499999999999]
[null,null,15520,5.4810549999999996,0.125475]
[null,null,15530,5.4652409999999998,0.113048]
[null,null,15540,5.4494639999999999,0.102133]
[null,null,15550,5.4337200000000001,9.2718999999999996E-2]
[null,null,15560,5.4180089999999996,8.4627999999999995E-2]
[null,null,15570,5.4023329999999996,7.7645000000000006E-2]
[null,null,15580,5.386698,7.1594000000000005E-2]
[null,null,15590,5.3711159999999998,6.6317000000000001E-2]
[null,null,15600,5.3555390000000003,6.1677000000000003E-2]
[null,null,15610,5.3396879999999998,5.7553E-2]
[null,null,15620,5.3242229999999999,5.3894999999999998E-2]
[null,null,15630,5.3087970000000002,5.0613999999999999E-2]
[null,null,15640,5.2934070000000002,4.7650999999999999E-2]
[null,null,15650,5.2780500000000004,4.4961000000000001E-2]
[null,null,15660,5.2627220000000001,4.2512000000000001E-2]
[null,null,15670,5.2474230000000004,4.0274999999999998E-2]
[null,null,15680,5.2321540000000004,3.8220999999999998E-2]
[null,null,15690,5.2169179999999997,3.6330000000000001E-2]
[null,null,15700,5.2017179999999996,3.4581000000000001E-2]
[null,null,15710,5.1865540000000001,3.2960999999999997E-2]
[null,null,15720,5.1714260000000003,3.1459000000000001E-2]
[null,null,15730,5.1563350000000003,3.0065999999999999E-2]
[null,null,15740,5.1412779999999998,2.8768999999999999E-2]
[null,null,15750,5.1262530000000002,2.7560000000000001E-2]
[null,null,15760,5.1110920000000002,2.6432000000000001E-2]
[null,null,15770,5.0962379999999996,2.5387E-2]
[null,null,15780,5.0813170000000003,2.4419E-2]
[null,null,15790,5.0664490000000004,2.3539999999999998E-2]
[null,null,15800,5.051628,2.2772000000000001E-2]
[null,null,15810,5.0368490000000001,2.2135999999999999E-2]
[null,null,15820,5.0221090000000004,2.1649999999999999E-2]
[null,null,15830,5.0074050000000003,2.1371999999999999E-2]
[null,null,15840,4.9927349999999997,2.1392999999999999E-2]
[null,null,15850,4.9781000000000004,2.1812000000000002E-2]
[null,null,15860,4.9635059999999998,2.2668000000000001E-2]
[null,null,15870,4.9489580000000002,2.3768999999999998E-2]
[null,null,15880,4.9344619999999999,2.4483999999999999E-2]
[null,null,15890,4.9200200000000001,2.4514000000000001E-2]
[null,null,15900,4.9056280000000001,2.4060999999999999E-2]
[null,null,15910,4.8912769999999997,2.3140999999999998E-2]
[null,null,15920,4.874549,2.1916999999999999E-2]
[null,null,15930,4.9274139999999997,2.0191000000000001E-2]
[null,null,15940,4.913481,1.8884999999999999E-2]
[null,null,15950,4.8994580000000001,1.7632999999999999E-2]
[null,null,15960,4.8854030000000002,1.6441999999999998E-2]
[null,null,15970,4.8713379999999997,1.5322000000000001E-2]
[null,null,15980,4.8572819999999997,1.4286999999999999E-2]
[null,null,15990,4.8432539999999999,1.3358999999999999E-2]
[null,null,16000,4.8292710000000003,1.2581999999999999E-2]
[null,null,16010,4.8153439999999996,1.2026E-2]
[null,null,16020,4.8014760000000001,1.1741E-2]
[null,null,16030,4.7876630000000002,1.1716000000000001E-2]
[null,null,16040,4.7738969999999998,1.1858E-2]
[null,null,16050,4.7601659999999999,1.2041E-2]
[null,null,16060,4.7464630000000003,1.2171E-2]
[null,null,16070,4.7327919999999999,1.221E-2]
[null,null,16080,4.7202859999999998,1.2161999999999999E-2]
[null,null,16090,4.7059990000000003,1.2035000000000001E-2]
[null,null,16100,4.6923959999999996,1.1854999999999999E-2]
[null,null,16110,4.678852,1.1648E-2]
[null,null,16120,4.6653650000000004,1.1433E-2]
[null,null,16130,4.6519339999999998,1.1207999999999999E-2]
[null,null,16140,4.6385480000000001,1.0971E-2]
[null,null,16150,4.6251949999999997,1.0722000000000001E-2]
[null,null,16160,4.6118639999999997,1.0465E-2]
[null,null,16170,4.5985490000000002,1.0192E-2]
[null,null,16180,4.5852490000000001,9.8790000000000006E-3]
[null,null,16190,4.5719750000000001,9.4830000000000001E-3]
[null,null,16200,4.5587410000000004,9.0130000000000002E-3]
[null,null,16210,4.5455690000000004,8.6049999999999998E-3]
[null,null,16220,4.5324819999999999,8.3009999999999994E-3]
[null,null,16230,4.519514,8.0370000000000007E-3]
[null,null,16240,4.497871,7.7380000000000001E-3]
[null,null,16250,4.5014209999999997,7.4469999999999996E-3]
[null,null,16260,4.4884719999999998,7.1840000000000003E-3]
[null,null,16270,4.4756239999999998,6.9150000000000001E-3]
[null,null,16280,4.4628220000000001,6.6839999999999998E-3]
[null,null,16290,4.4500440000000001,6.5449999999999996E-3]
[null,null,16300,4.4372819999999997,6.4440000000000001E-3]
[null,null,16310,4.4245369999999999,6.3210000000000002E-3]
[null,null,16320,4.4118149999999998,6.1720000000000004E-3]
[null,null,16330,4.3991280000000001,6.0080000000000003E-3]
[null,null,16340,4.3864850000000004,5.8370000000000002E-3]
[null,null,16350,4.3738950000000001,5.6610000000000002E-3]
[null,null,16360,4.3613590000000002,5.476E-3]
[null,null,16370,4.3488749999999996,5.2839999999999996E-3]
[null,null,16380,4.3364380000000002,5.0949999999999997E-3]
[null,null,16390,4.3240470000000002,4.9090000000000002E-3]
[null,null,16400,4.3119870000000002,4.7210000000000004E-3]
[null,null,16410,4.2996350000000003,4.5129999999999997E-3]
[null,null,16420,4.2873099999999997,4.2859999999999999E-3]
[null,null,16430,4.2750120000000003,4.0249999999999999E-3]
[null,null,16440,4.2627540000000002,3.7309999999999999E-3]
[null,null,16450,4.2505470000000001,3.424E-3]
[null,null,16460,4.2383949999999997,3.1589999999999999E-3]
[null,null,16470,4.2262969999999997,3.0070000000000001E-3]
[null,null,16480,4.214245,3.0240000000000002E-3]
[null,null,16490,4.202223,3.2320000000000001E-3]
[null,null,16500,4.190213,3.617E-3]
[null,null,16510,4.1781980000000001,4.1679999999999998E-3]
[null,null,16520,4.1661700000000002,4.8770000000000003E-3]
[null,null,16530,4.1541290000000002,5.7330000000000002E-3]
[null,null,16540,4.1420940000000002,6.7219999999999997E-3]
[null,null,16550,4.1301110000000003,7.8200000000000006E-3]
[null,null,16560,4.18431,1.0264000000000001E-2]
[null,null,16570,4.1721529999999998,1.1139E-2]
[null,null,16580,4.1600159999999997,1.231E-2]
[null,null,16590,4.1480100000000002,1.6910999999999999E-2]
[null,null,16600,4.1361189999999999,2.5284999999999998E-2]
[null,null,16610,4.1243220000000003,2.7156E-2]
[null,null,16620,4.1125949999999998,2.3050999999999999E-2]
[null,null,16630,4.1009099999999998,1.8960999999999999E-2]
[null,null,16640,4.0892480000000004,1.5913E-2]
[null,null,16650,4.0775969999999999,1.3676000000000001E-2]
[null,null,16660,4.0659549999999998,1.1989E-2]
[null,null,16670,4.0543329999999997,1.0673E-2]
[null,null,16680,4.0427439999999999,9.6159999999999995E-3]
[null,null,16690,4.0312029999999996,8.7690000000000008E-3]
[null,null,16700,4.0197200000000004,8.1030000000000008E-3]
[null,null,16710,4.0083000000000002,7.5760000000000003E-3]
[null,null,16720,3.99614,7.1440000000000002E-3]
[null,null,16730,3.987873,6.777E-3]
[null,null,16740,3.97662,6.4780000000000003E-3]
[null,null,16750,3.9653649999999998,6.2240000000000004E-3]
[null,null,16760,3.9541189999999999,6.0089999999999996E-3]
[null,null,16770,3.9428899999999998,5.836E-3]
[null,null,16780,3.9316879999999998,5.7019999999999996E-3]
[null,null,16790,3.9205239999999999,5.607E-3]
[null,null,16800,3.9094069999999999,5.5510000000000004E-3]
[null,null,16810,3.898342,5.535E-3]
[null,null,16820,3.8873280000000001,5.5599999999999998E-3]
[null,null,16830,3.8763570000000001,5.6259999999999999E-3]
[null,null,16840,3.865424,5.7340000000000004E-3]
[null,null,16850,3.8545229999999999,5.8760000000000001E-3]
[null,null,16860,3.843658,6.0499999999999998E-3]
[null,null,16870,3.8328500000000001,6.2599999999999999E-3]
[null,null,16880,3.8277559999999999,6.535E-3]
[null,null,16890,3.81595,6.8230000000000001E-3]
[null,null,16900,3.8052069999999998,7.1469999999999997E-3]
[null,null,16910,3.7945220000000002,7.5170000000000002E-3]
[null,null,16920,3.7838889999999998,7.9410000000000001E-3]
[null,null,16930,3.7732990000000002,8.4229999999999999E-3]
[null,null,16940,3.7627410000000001,8.9960000000000005E-3]
[null,null,16950,3.7522069999999998,9.6860000000000002E-3]
[null,null,16960,3.741695,1.0484E-2]
[null,null,16970,3.7312080000000001,1.1339999999999999E-2]
[null,null,16980,3.7207560000000002,1.2132E-2]
[null,null,16990,3.7103489999999999,1.2630000000000001E-2]
[null,null,17000,3.6999919999999999,1.2548999999999999E-2]
[null,null,17010,3.6896840000000002,1.1794000000000001E-2]
[null,null,17020,3.6794150000000001,1.0498E-2]
[null,null,17030,3.669168,8.9379999999999998E-3]
[null,null,17040,3.6579440000000001,7.3740000000000003E-3]
[null,null,17050,3.6656080000000002,5.8459999999999996E-3]
[null,null,17060,3.6555520000000001,4.6470000000000001E-3]
[null,null,17070,3.6454680000000002,3.6640000000000002E-3]
[null,null,17080,3.6353960000000001,2.9069999999999999E-3]
[null,null,17090,3.6253609999999998,2.4069999999999999E-3]
[null,null,17100,3.615383,2.2070000000000002E-3]
[null,null,17110,3.6054719999999998,2.2829999999999999E-3]
[null,null,17120,3.595628,2.5300000000000001E-3]
[null,null,17130,3.5858409999999998,2.8189999999999999E-3]
[null,null,17140,3.5760960000000002,3.0500000000000002E-3]
[null,null,17150,3.5663770000000001,3.16E-3]
[null,null,17160,3.5566759999999999,3.1220000000000002E-3]
[null,null,17170,3.5469909999999998,2.9499999999999999E-3]
[null,null,17180,3.537334,2.6840000000000002E-3]
[null,null,17190,3.5277289999999999,2.3679999999999999E-3]
[null,null,17200,3.5192489999999998,2.0460000000000001E-3]
[null,null,17210,3.5094639999999999,1.7409999999999999E-3]
[null,null,17220,3.5000279999999999,1.4909999999999999E-3]
[null,null,17230,3.4906389999999998,1.3159999999999999E-3]
[null,null,17240,3.4812859999999999,1.2179999999999999E-3]
[null,null,17250,3.4719530000000001,1.188E-3]
[null,null,17260,3.4626250000000001,1.2340000000000001E-3]
[null,null,17270,3.4533,1.377E-3]
[null,null,17280,3.443988,1.6310000000000001E-3]
[null,null,17290,3.434707,2E-3]
[null,null,17300,3.425481,2.4710000000000001E-3]
[null,null,17310,3.4163299999999999,2.9369999999999999E-3]
[null,null,17320,3.4072629999999999,3.1440000000000001E-3]
[null,null,17330,3.3982770000000002,2.9979999999999998E-3]
[null,null,17340,3.3893550000000001,2.7680000000000001E-3]
[null,null,17350,3.3804569999999998,2.6340000000000001E-3]
[null,null,17360,3.3751090000000001,2.594E-3]
[null,null,17370,3.3577849999999998,2.5079999999999998E-3]
[null,null,17380,3.3490190000000002,2.5799999999999998E-3]
[null,null,17390,3.3402400000000001,2.6700000000000001E-3]
[null,null,17400,3.331467,2.7490000000000001E-3]
[null,null,17410,3.3227159999999998,2.8110000000000001E-3]
[null,null,17420,3.3139970000000001,2.8960000000000001E-3]
[null,null,17430,3.3053180000000002,3.0140000000000002E-3]
[null,null,17440,3.2966769999999999,3.153E-3]
[null,null,17450,3.2880699999999998,3.3040000000000001E-3]
[null,null,17460,3.2794910000000002,3.4640000000000001E-3]
[null,null,17470,3.27094,3.6340000000000001E-3]
[null,null,17480,3.2624209999999998,3.8180000000000002E-3]
[null,null,17490,3.2539440000000002,4.0130000000000001E-3]
[null,null,17500,3.2455210000000001,4.2129999999999997E-3]
[null,null,17510,3.2371599999999998,4.4200000000000003E-3]
[null,null,17520,3.2284090000000001,4.6369999999999996E-3]
[null,null,17530,3.221028,4.8719999999999996E-3]
[null,null,17540,3.2128359999999998,5.1180000000000002E-3]
[null,null,17550,3.2046429999999999,5.3839999999999999E-3]
[null,null,17560,3.1964459999999999,5.6709999999999998E-3]
[null,null,17570,3.1882440000000001,5.9769999999999997E-3]
[null,null,17580,3.180053,6.2940000000000001E-3]
[null,null,17590,3.1719010000000001,6.6189999999999999E-3]
[null,null,17600,3.1638220000000001,6.9560000000000004E-3]
[null,null,17610,3.1558459999999999,7.3130000000000001E-3]
[null,null,17620,3.1479840000000001,7.7010000000000004E-3]
[null,null,17630,3.1402199999999998,8.1270000000000005E-3]
[null,null,17640,3.1325080000000001,8.5880000000000001E-3]
[null,null,17650,3.1247699999999998,9.0989999999999994E-3]
[null,null,17660,3.116879,9.7000000000000003E-3]
[null,null,17670,3.1085229999999999,1.0418E-2]
[null,null,17680,4.1067130000000001,8.9859999999999992E-3]
[null,null,17690,4.0939629999999996,1.0470999999999999E-2]
[null,null,17700,4.0845789999999997,1.2267E-2]
[null,null,17710,4.0750029999999997,1.4003E-2]
[null,null,17720,4.0653740000000003,1.4463999999999999E-2]
[null,null,17730,4.055777,1.248E-2]
[null,null,17740,4.0462680000000004,9.1039999999999992E-3]
[null,null,17750,4.0368690000000003,5.836E-3]
[null,null,17760,4.0275790000000002,3.1020000000000002E-3]
[null,null,17770,4.0183720000000003,8.8000000000000003E-4]
[null,null,17780,4.0092160000000003,1.3270000000000001E-3]
[null,null,17790,4.0000809999999998,3.032E-3]
[null,null,17800,3.9909469999999998,4.4270000000000004E-3]
[null,null,17810,3.9818099999999998,5.3429999999999997E-3]
[null,null,17820,3.97268,5.7349999999999996E-3]
[null,null,17830,3.9635699999999998,5.7270000000000003E-3]
[null,null,17840,3.9540250000000001,5.5149999999999999E-3]
[null,null,17850,3.9464239999999999,5.2630000000000003E-3]
[null,null,17860,3.9375230000000001,5.0410000000000003E-3]
[null,null,17870,3.928671,4.901E-3]
[null,null,17880,3.9198620000000002,4.8469999999999997E-3]
[null,null,17890,3.9110819999999999,4.862E-3]
[null,null,17900,3.902323,4.921E-3]
[null,null,17910,3.893583,5.0029999999999996E-3]
[null,null,17920,3.8848690000000001,5.1000000000000004E-3]
[null,null,17930,3.8761920000000001,5.2090000000000001E-3]
[null,null,17940,3.8675639999999998,5.3290000000000004E-3]
[null,null,17950,3.8589959999999999,5.457E-3]
[null,null,17960,3.850492,5.5880000000000001E-3]
[null,null,17970,3.84205,5.7270000000000003E-3]
[null,null,17980,3.833666,5.8799999999999998E-3]
[null,null,17990,3.8253460000000001,6.0460000000000002E-3]
[null,null,18000,3.8226270000000002,6.1859999999999997E-3]
[null,null,18010,3.8133219999999999,6.4149999999999997E-3]
[null,null,18020,3.8050519999999999,6.7190000000000001E-3]
[null,null,18030,3.796805,7.1110000000000001E-3]
[null,null,18040,3.7885939999999998,7.5810000000000001E-3]
[null,null,18050,3.7804220000000002,8.1119999999999994E-3]
[null,null,18060,3.7722920000000002,8.6359999999999996E-3]
[null,null,18070,3.764205,9.1090000000000008E-3]
[null,null,18080,3.756157,9.5460000000000007E-3]
[null,null,18090,3.7481469999999999,9.9869999999999994E-3]
[null,null,18100,3.7401710000000001,1.0486000000000001E-2]
[null,null,18110,3.7322289999999998,1.11E-2]
[null,null,18120,3.7243210000000002,1.1837E-2]
[null,null,18130,3.7164459999999999,1.2626E-2]
[null,null,18140,3.7086060000000001,1.3421000000000001E-2]
[null,null,18150,3.7007919999999999,1.4187E-2]
[null,null,18160,3.6939009999999999,1.4917E-2]
[null,null,18170,3.6814360000000002,1.5602E-2]
[null,null,18180,3.6737039999999999,1.6315E-2]
[null,null,18190,3.666032,1.7049999999999999E-2]
[null,null,18200,3.6584110000000001,1.7818000000000001E-2]
[null,null,18210,3.6508430000000001,1.8627000000000001E-2]
[null,null,18220,3.6433300000000002,1.9494999999999998E-2]
[null,null,18230,3.635872,2.0431999999999999E-2]
[null,null,18240,3.6284640000000001,2.1444999999999999E-2]
[null,null,18250,3.6211009999999999,2.2544000000000002E-2]
[null,null,18260,3.6137730000000001,2.3737000000000001E-2]
[null,null,18270,3.6064759999999998,2.503E-2]
[null,null,18280,3.5992069999999998,2.6414E-2]
[null,null,18290,3.5919690000000002,2.7851000000000001E-2]
[null,null,18300,3.5847669999999998,2.9239000000000001E-2]
[null,null,18310,3.5776080000000001,3.0377000000000001E-2]
[null,null,18320,3.5695199999999998,3.0890999999999998E-2]
[null,null,18330,3.562894,3.0179000000000001E-2]
[null,null,18340,3.555917,2.7356999999999999E-2]
[null,null,18350,3.548969,2.1592E-2]
[null,null,18360,3.5420419999999999,1.2718E-2]
[null,null,18370,3.5351279999999998,1.508E-3]
[null,null,18380,3.5282279999999999,1.1117E-2]
[null,null,18390,3.52135,2.4819999999999998E-2]
[null,null,18400,3.514513,4.0162999999999997E-2]
[null,null,18410,3.5077370000000001,5.8187000000000003E-2]
[null,null,18420,3.501042,7.9330999999999999E-2]
[null,null,18430,3.4944350000000002,0.100076]
[null,null,18440,3.4879060000000002,0.109859]
[null,null,18450,3.4814259999999999,0.103003]
[null,null,18460,3.474939,8.8355000000000003E-2]
[null,null,18470,3.4683510000000002,7.4181999999999998E-2]
[null,null,18480,3.4659,6.2754000000000004E-2]
[null,null,18490,3.0911240000000002,5.4827000000000001E-2]
[null,null,18500,3.0844900000000002,4.8035000000000001E-2]
[null,null,18510,3.0775709999999998,4.2653000000000003E-2]
[null,null,18520,3.070557,3.8303999999999998E-2]
[null,null,18530,3.063526,3.4708000000000003E-2]
[null,null,18540,3.0565319999999998,3.168E-2]
[null,null,18550,3.0496099999999999,2.9103E-2]
[null,null,18560,3.0427740000000001,2.6882E-2]
[null,null,18570,3.0360209999999999,2.4941999999999999E-2]
[null,null,18580,3.0293359999999998,2.3224999999999999E-2]
[null,null,18590,3.0226959999999998,2.1693E-2]
[null,null,18600,3.0160809999999998,2.0320000000000001E-2]
[null,null,18610,3.0094799999999999,1.9091E-2]
[null,null,18620,3.0028869999999999,1.7989000000000002E-2]
[null,null,18630,2.9963039999999999,1.6996000000000001E-2]
[null,null,18640,2.9889019999999999,1.6091000000000001E-2]
[null,null,18650,2.9829819999999998,1.5270000000000001E-2]
[null,null,18660,2.976553,1.4515999999999999E-2]
[null,null,18670,2.9701759999999999,1.3821E-2]
[null,null,18680,2.963848,1.3180000000000001E-2]
[null,null,18690,2.9575629999999999,1.2593999999999999E-2]
[null,null,18700,2.9513159999999998,1.2061000000000001E-2]
[null,null,18710,2.9451070000000001,1.1575E-2]
[null,null,18720,2.9389349999999999,1.1133000000000001E-2]
[null,null,18730,2.932804,1.0734E-2]
[null,null,18740,2.9267150000000002,1.0385999999999999E-2]
[null,null,18750,2.9206639999999999,1.0096000000000001E-2]
[null,null,18760,2.9146420000000002,9.8539999999999999E-3]
[null,null,18770,2.908633,9.6259999999999991E-3]
[null,null,18780,2.9026179999999999,9.4269999999999996E-3]
[null,null,18790,2.8965619999999999,9.2929999999999992E-3]
[null,null,18800,2.9156260000000001,9.3559999999999997E-3]
[null,null,18810,2.9055200000000001,9.4479999999999998E-3]
[null,null,18820,2.899661,9.7059999999999994E-3]
[null,null,18830,2.8938120000000001,1.0029E-2]
[null,null,18840,2.88802,9.9450000000000007E-3]
[null,null,18850,2.882307,8.9730000000000001E-3]
[null,null,18860,2.8766790000000002,7.5690000000000002E-3]
[null,null,18870,2.87113,6.3579999999999999E-3]
[null,null,18880,2.8656419999999998,5.4790000000000004E-3]
[null,null,18890,2.8601930000000002,4.8799999999999998E-3]
[null,null,18900,2.854762,4.5110000000000003E-3]
[null,null,18910,2.8493390000000001,4.3480000000000003E-3]
[null,null,18920,2.8439239999999999,4.3379999999999998E-3]
[null,null,18930,2.8385250000000002,4.3680000000000004E-3]
[null,null,18940,2.8331590000000002,4.3189999999999999E-3]
[null,null,18950,2.8278349999999999,4.1640000000000002E-3]
[null,null,18960,2.8227530000000001,3.9550000000000002E-3]
[null,null,18970,2.8167080000000002,3.7720000000000002E-3]
[null,null,18980,2.8115649999999999,3.6649999999999999E-3]
[null,null,18990,2.8064779999999998,3.6830000000000001E-3]
[null,null,19000,2.8014239999999999,3.8240000000000001E-3]
[null,null,19010,2.7963900000000002,4.0330000000000001E-3]
[null,null,19020,2.7913749999999999,4.2290000000000001E-3]
[null,null,19030,2.7863850000000001,4.3480000000000003E-3]
[null,null,19040,2.7814350000000001,4.3639999999999998E-3]
[null,null,19050,2.7765390000000001,4.2779999999999997E-3]
[null,null,19060,2.7717079999999998,4.1099999999999999E-3]
[null,null,19070,2.766947,3.8769999999999998E-3]
[null,null,19080,2.7622490000000002,3.5929999999999998E-3]
[null,null,19090,2.7575980000000002,3.264E-3]
[null,null,19100,2.7529710000000001,2.911E-3]
[null,null,19110,2.7483369999999998,2.5609999999999999E-3]
[null,null,19120,2.7325780000000002,2.3509999999999998E-3]
[null,null,19130,2.7286670000000002,2.2880000000000001E-3]
[null,null,19140,2.7241939999999998,2.5089999999999999E-3]
[null,null,19150,2.7197420000000001,2.9750000000000002E-3]
[null,null,19160,2.7153290000000001,3.5170000000000002E-3]
[null,null,19170,2.7109670000000001,3.9569999999999996E-3]
[null,null,19180,2.706658,4.1859999999999996E-3]
[null,null,19190,2.7023969999999999,4.241E-3]
[null,null,19200,2.6981739999999999,4.1960000000000001E-3]
[null,null,19210,2.6939799999999998,4.1110000000000001E-3]
[null,null,19220,2.6898089999999999,4.0280000000000003E-3]
[null,null,19230,2.6856599999999999,3.9750000000000002E-3]
[null,null,19240,2.6815410000000002,3.9439999999999996E-3]
[null,null,19250,2.6774610000000001,3.908E-3]
[null,null,19260,2.6734339999999999,3.8679999999999999E-3]
[null,null,19270,2.6694629999999999,3.8219999999999999E-3]
[null,null,19280,2.66669,3.7680000000000001E-3]
[null,null,19290,2.6562100000000002,3.689E-3]
[null,null,19300,2.6523159999999999,3.6380000000000002E-3]
[null,null,19310,2.6484860000000001,3.5959999999999998E-3]
[null,null,19320,2.6446930000000002,3.5599999999999998E-3]
[null,null,19330,2.6409310000000001,3.5349999999999999E-3]
[null,null,19340,2.6372049999999998,3.529E-3]
[null,null,19350,2.6335229999999998,3.5469999999999998E-3]
[null,null,19360,2.629893,3.5920000000000001E-3]
[null,null,19370,2.6263200000000002,3.666E-3]
[null,null,19380,2.6228020000000001,3.771E-3]
[null,null,19390,2.6193309999999999,3.9069999999999999E-3]
[null,null,19400,2.6158920000000001,4.0769999999999999E-3]
[null,null,19410,2.6124719999999999,4.28E-3]
[null,null,19420,2.6090589999999998,4.5129999999999997E-3]
[null,null,19430,2.6056409999999999,4.777E-3]
[null,null,19440,2.5993240000000002,5.091E-3]
[null,null,19450,2.5968079999999998,5.4559999999999999E-3]
[null,null,19460,2.59355,5.9069999999999999E-3]
[null,null,19470,2.59036,6.4989999999999996E-3]
[null,null,19480,2.587237,7.2880000000000002E-3]
[null,null,19490,2.584174,8.3070000000000001E-3]
[null,null,19500,2.5811519999999999,9.5940000000000001E-3]
[null,null,19510,2.5781499999999999,1.1254E-2]
[null,null,19520,2.5751499999999998,1.3474E-2]
[null,null,19530,2.5721449999999999,1.6551E-2]
[null,null,19540,2.5691449999999998,2.0820999999999999E-2]
[null,null,19550,2.566176,2.5569999999999999E-2]
[null,null,19560,2.5632769999999998,2.5152000000000001E-2]
[null,null,19570,2.5604930000000001,1.7916000000000001E-2]
[null,null,19580,2.5578669999999999,1.3390000000000001E-2]
[null,null,19590,2.555444,1.2154999999999999E-2]
[null,null,19600,2.553973,1.1445E-2]
[null,null,19610,2.2951649999999999,7.8130000000000005E-3]
[null,null,19620,2.2919529999999999,6.9329999999999999E-3]
[null,null,19630,2.2888350000000002,6.1089999999999998E-3]
[null,null,19640,2.2857159999999999,5.359E-3]
[null,null,19650,2.2825579999999999,4.6839999999999998E-3]
[null,null,19660,2.2793540000000001,4.0899999999999999E-3]
[null,null,19670,2.276119,3.5669999999999999E-3]
[null,null,19680,2.272878,3.107E-3]
[null,null,19690,2.2696640000000001,2.715E-3]
[null,null,19700,2.266502,2.4090000000000001E-3]
[null,null,19710,2.2634089999999998,2.2079999999999999E-3]
[null,null,19720,2.260386,2.1129999999999999E-3]
[null,null,19730,2.257425,2.0960000000000002E-3]
[null,null,19740,2.2545069999999998,2.1189999999999998E-3]
[null,null,19750,2.2516099999999999,2.1610000000000002E-3]
[null,null,19760,2.2486709999999999,2.2139999999999998E-3]
[null,null,19770,2.2455059999999998,2.2690000000000002E-3]
[null,null,19780,2.2426490000000001,2.3289999999999999E-3]
[null,null,19790,2.2398340000000001,2.4009999999999999E-3]
[null,null,19800,2.2370700000000001,2.4859999999999999E-3]
[null,null,19810,2.2343660000000001,2.575E-3]
[null,null,19820,2.2317260000000001,2.6619999999999999E-3]
[null,null,19830,2.2291449999999999,2.748E-3]
[null,null,19840,2.2266119999999998,2.8319999999999999E-3]
[null,null,19850,2.22411,2.9090000000000001E-3]
[null,null,19860,2.221625,2.9659999999999999E-3]
[null,null,19870,2.2191489999999998,2.9870000000000001E-3]
[null,null,19880,2.216682,2.9989999999999999E-3]
[null,null,19890,2.2142369999999998,3.0790000000000001E-3]
[null,null,19900,2.21184,3.212E-3]
[null,null,19910,2.209549,3.3579999999999999E-3]
[null,null,19920,2.1881879999999998,3.4880000000000002E-3]
[null,null,19930,2.1928809999999999,3.6459999999999999E-3]
[null,null,19940,2.1906289999999999,3.79E-3]
[null,null,19950,2.188491,3.9639999999999996E-3]
[null,null,19960,2.1864330000000001,4.267E-3]
[null,null,19970,2.184431,4.718E-3]
[null,null,19980,2.1824669999999999,5.1450000000000003E-3]
[null,null,19990,2.1805289999999999,5.4840000000000002E-3]
[null,null,20000,2.1786099999999999,5.7720000000000002E-3]
[null,null,20010,2.1767110000000001,6.0390000000000001E-3]
[null,null,20020,2.1748409999999998,6.2979999999999998E-3]
[null,null,20030,2.173006,6.5500000000000003E-3]
[null,null,20040,2.171217,6.7930000000000004E-3]
[null,null,20050,2.1694789999999999,7.0299999999999998E-3]
[null,null,20060,2.1677940000000002,7.2649999999999998E-3]
[null,null,20070,2.1661600000000001,7.4840000000000002E-3]
[null,null,20080,2.1652049999999998,7.6509999999999998E-3]
[null,null,20090,2.1623800000000002,7.7099999999999998E-3]
[null,null,20100,2.1608160000000001,7.6090000000000003E-3]
[null,null,20110,2.1592910000000001,7.2690000000000003E-3]
[null,null,20120,2.1578010000000001,6.6169999999999996E-3]
[null,null,20130,2.1563490000000001,5.6179999999999997E-3]
[null,null,20140,2.154944,4.2960000000000003E-3]
[null,null,20150,2.1535890000000002,2.7390000000000001E-3]
[null,null,20160,2.152288,1.088E-3]
[null,null,20170,2.1510359999999999,8.83E-4]
[null,null,20180,2.149826,2.5820000000000001E-3]
[null,null,20190,2.1486450000000001,4.3610000000000003E-3]
[null,null,20200,2.1474799999999998,6.1929999999999997E-3]
[null,null,20210,2.1463169999999998,8.1089999999999999E-3]
[null,null,20220,2.1451370000000001,1.0153000000000001E-2]
[null,null,20230,2.143885,1.2367E-2]
[null,null,20240,2.0928520000000002,1.504E-2]
[null,null,20250,2.0942219999999998,1.7492000000000001E-2]
[null,null,20260,2.093334,1.9719E-2]
[null,null,20270,2.0924830000000001,2.1284999999999998E-2]
[null,null,20280,2.0916760000000001,2.1826000000000002E-2]
[null,null,20290,2.0909200000000001,2.1187000000000001E-2]
[null,null,20300,2.0902150000000002,1.9574999999999999E-2]
[null,null,20310,2.0895579999999998,1.7572999999999998E-2]
[null,null,20320,2.0889440000000001,1.5585E-2]
[null,null,20330,2.088368,1.3788E-2]
[null,null,20340,2.0878269999999999,1.2229E-2]
[null,null,20350,2.0873210000000002,1.0895999999999999E-2]
[null,null,20360,2.0868519999999999,9.7470000000000005E-3]
[null,null,20370,2.0864220000000002,8.744E-3]
[null,null,20380,2.086036,7.8750000000000001E-3]
[null,null,20390,2.0857039999999998,7.1180000000000002E-3]
[null,null,20400,2.0853419999999998,6.4549999999999998E-3]
[null,null,20410,2.0850119999999999,5.855E-3]
[null,null,20420,2.0847920000000002,5.3489999999999996E-3]
[null,null,20430,2.084606,4.9119999999999997E-3]
[null,null,20440,2.0844559999999999,4.5399999999999998E-3]
[null,null,20450,2.0843389999999999,4.2399999999999998E-3]
[null,null,20460,2.0842559999999999,4.0200000000000001E-3]
[null,null,20470,2.084206,3.8860000000000001E-3]